### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 1st November 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders and Mr Kumail Haider (L.B. Hounslow) and Miss Emma McDonald (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – All Hoppers full with complete covering of algae on Hoppers 1 & 3 and sludge crust on Hopper 2 - requires draining/over-pumping. Tank 1B – Tank empty – Approx. 75% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 approx 50% full with sludge crust and Hopper 2 approx. 30% full - requires draining/over-pumping. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 80% full with Sludge crust on Hoppers 1 & 3 - requires draining/over-pumping. Tank 3A – Tank empty – Approx. 75% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers approx. 75% full - requires draining/over-pumping. Tank 3B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers full with sludge crust on Hoppers 1 & 2 - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 20% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 7A – Tank in process of being returned to works – All Amajets in use. Tank 7B – Tank backfilling – approx. 60% of Tank and all Hoppers covered – requires draining/over-pumping. – remainder of tank completely covered by grit and sludge – requires further flushing. Tank 8A – Tank backfilling – approx. 60% of Tank and all Hoppers covered – requires draining/over-pumping. Remainder of Tank clean. Tank 8B – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – All Hoppers full with sludge and algae crust - requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 10% capacity. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 28/10/22; 0; 389; 122; 511; 632; 1143. |  |
| Complaints The Council received no complaints by email from MRAG in the preceding week. Thames Water controller advised that they had received no direct complaints in the preceding week. The Council directly received no complaints by email in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .004; ppm; 14:27. Monitor 2; .001; ppm; 14:27. Monitor 3; .004; ppm; 14:27. Monitor 4; .000; ppm; 14:27. Monitor 5; .004; ppm; 14:27. Monitor 6; .006; ppm; 14:27. Monitor 7; .000; ppm; 14:27. Monitor 8; .005; ppm; 14:27. Monitor 9; .004; ppm; 14:27. Monitor 10; .005; ppm; 14:27. Monitor 11; .004; ppm; 14:27. Monitor 12; .006; ppm; 14:27. Monitor 13; .005; ppm; 14:27. Wind Speed; 5.3; mph; 14:27. Wind Direction; 186°; 14:27. |  |
| Odour Log (Thames): Wednesday 26th October 2022: AM – Cool – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: “Abel (sic) calibrating odour monitors.” Actions: No data. PM – Cool – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes No data. Actions: No data. Thursday 27th October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data PM – Cool – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data Actions: No data. Friday 28th October 2022: AM – warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Rain. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Saturday 29th October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM10 0.016 09:38-09:53.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Sunday 30th October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Monday 31st October 2022: AM – Warm – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Rain. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 1st November 2022: AM – Cool – Rainy with Sunny Spells. All OMU’s in use. Observations/Complaints: ”No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes No data. Actions: No data. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. Digester 6 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. Digester 7 - In use – seal level approx. 6ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 8 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 9 - In use – seal level approx. 2ft below coping stones – Seal weak and bubbling. Digester 10 - In use – seal level approx. 4ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas - Tank bubbling vigorously with ongoing spill – requires clean-up and anti-foam. Digester 11 - In use – seal level approx. 3ft below coping stones – Seal weak and bubbling. Digester 12 - In use – seal level approx. 4ft below coping stones – Seal weak and bubbling. Digester 13 - In use – seal level approx. 4ft below coping stones - Seal weak and bubbling - Tank bubbling vigorously with ongoing spill – requires clean-up and anti-foam. Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 4ft below coping stones - Seal weak and bubbling. Digester 18 – In use – seal level approx. 5ft below coping stones - Seal weak and bubbling. Digester 19 – In use – seal level approx. 6ft below coping stones - Seal weak and bubbling. Digester 20 - In use – seal level approx. 6ft below coping stones - Seal weak and bubbling. |  |
| GENERAL Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter currently missing and awaiting replacement following damage – opening has been screened temporarily. Imported Sludge Total of 106 Imports in preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. Tanks 71 & 73 currently out of service and undergoing complete overhaul – Contractors on site. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use – no issues. Number 12 drained down. New Works (West Side) Battery E No issues. Pasteurisation Plant Streams 1, 2, 6 and 11 out of service. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (full) uncovered (tarpaulin pulled back) and 1x 10-Yard Rag skip (covered) at rear of Sludge Screening House. 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. 1x open container General Waste skip in Service Road at rear of Pasteurisation Plant. |  |

Odour Control Unit (OCU) performance monitoring – No Data

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | No data | 0.2 | Unknown |
| East OCU | No data | 0.05 | Unknown |
| West inlet OCU | No data | 0.05 | Unknown |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | No data | 0.6 | Unknown |
| Transfer PS inlet | No data | Unknown | Unknown |
| Transfer PS outlet | No data | 0.5 | Unknown |
| New West inlet (OCU11) | No data | 0.5 | Unknown |
| Pasteurisation Plant (OCU12) | No data | 0.5 | Unknown |
| GBT Plant OCU Outlet | No data | Unknown | Unknown |