### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 25 October 2022 |  |
| --- | --- |
| Attendees: Mr Kumail Haider and Mr Zaheer Kadri (L.B. Hounslow) and Miss Emma McDonald (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – All Hoppers <30%. Tank 1B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers <10% Tank 2A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers <10% Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers approx.70% requires draining/over-pumping. Tank 3A – Tank full all Amajets operational and returning. Tank 3B – Tank full all Amajets operational and returning. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to measure condition due to light. Tank 6A – Tank empty approx 50% covered by grit requires further flushing – All Hoppers <10% full. Tank 6B – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. <10% full - requires draining/over-pumping. Tank 7A – Tank backfilling >70% effluent and returing to storm –Amajets 1,2 &3 operational. Tank 7B – Tank backfilling >70% effluent and returning to storm –Amajets 1,2 &3 operational. Tank 8A – Tank backfilling – approx 70% effulent returning to storm. Amajets 1,2&3 operational. Tank 8B – Tank backfilling – approx 70% effulent returning to storm. Amajets 1,2&3 operational. Feed Channel - The level of effluent in both feed channels was approximately 30% capacity. |  |
| Complaints The Council received no complaints by email from MRAG in the preceding week. Thames Water controller advised that they had received no direct complaints in the preceding week. The Council directly received two complaints by online reports in the preceding week: 21/10/22 (19:35) from the area of Sussex Avenue – historic trace data checked for OMU’s in vicinity: OMU’s 1, 2 & 3 = .003. Wind= 228° Speed = 5.4mph 23/10/22 (16:16) from the area of Elmer Gardens – historic trace data checked for OMU’s in vicinity: OMU1 = .003, OMU2 = .002 & OMU3 = .000, Wind = 223° Speed = 4.7mph Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:11. Monitor 2; .001; ppm; 13:11. Monitor 3; -0.025; ppm; 13:11. Monitor 4; .003; ppm; 13:11. Monitor 5; .000; ppm; 13:11. Monitor 6; .003; ppm; 13:11. Monitor 7; .000; ppm; 13:11. Monitor 8; .005; ppm; 13:11. Monitor 9; .004; ppm; 13:11. Monitor 10; .004; ppm; 13:11. Monitor 11; .004; ppm; 13:11. Monitor 12; .005; ppm; 13:11. Monitor 13; .003; ppm; 13:11. Wind Speed; 3.174; mph; 13:11. Wind Direction; 202°; 13:11. |  |
| Odour Log (Thames): Wednesday 19th October 2022: AM – Warm – Sunny w/patchy clouds. All OMU’s in use. Observations/Complaints: “OM3 0.016ppm @06.10 & 0.017ppm @08.54 both spikes less than 15 minutes ” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes No data. Actions: No data. Thursday 20th October 2022: AM – Cool – Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data Actions: No data. Friday 21th October 2022: AM – Cool – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Rain. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Saturday 22nd October 2022: AM – Cool – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Cloudy All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data Actions: No data Sunday 23rd October 2022: AM – Cool – Rain. All OMU’s in use. Observations/Complaints: “OM3 spiked during 07.38-07.53 max 0.023ppm.” Operational Issues/Causes: “No data Actions: No data PM – Cool – Storms All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Monday 24th October 2022: AM – Warm – Rain. All OMU’s in use. Observations/Complaints: “OM10 @09.38 spiked for <15 minutes max 0.023ppm.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Patchy Rain. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Tuesday 25th October 2022: AM – Cool –Cloudy All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: Abel calibrating odour monitors . Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes No data Actions: No data # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 19/10/22; 0; 328; 679; 1007; 1088; 2095. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 2ft below coping stones - Seal good and crusty. Digester 6 - In use – seal level approx. 2ft below coping stones - Seal weak and bubbling. Digester 7 - In use – seal level approx. 4ft below coping stones - Seal weak and bubbling – historic spill – requires clean-up. Digester 8 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. Digester 9 - In use – seal level approx. 2ft below coping stones – Seal weak and bubbling. Digester 10 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas - Digester 11 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 12 - In use – seal level approx. 2ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Digester 14 – Not in use. Digester 15 – Not in use. Digester 16 – Not in use. Digester 17 - In use – seal level approx. 2ft below coping stones - Seal crusty and thick. Digester 18 – In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. Digester 19 – In use – seal level approx. 2” below coping stones - Seal weak and bubbling, minor historic spillage requires clean up. Digester 20 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. |  |
| GENERAL Large sludge spill from break in pipe servicing mobile screeners located at entrance to Digesters – area requires clean-up and flushing. Ongoing water leak from plant located at rear of Pasteurisation Plant. Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge Total Imports in preceding seven days = 2411m³. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. Tanks 71 & 73 currently out of service and undergoing complete overhaul – Contractors on site. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E No issues. Pasteurisation Plant Streams 1,2,6 and 11 out of service. 8/12 streams in operation. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) covered with tarpaulin & 1x 10-Yard Rag skip (covered). 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. |  |

Odour Control Unit (OCU) performance monitoring – 26/10/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.000 0.000 0.000 | 0.2 | Yes |
| East OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| West inlet OCU | 0.00 0.02 0.01 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.012 0.011 0.008 | 0.6 | Yes |
| Transfer PS inlet | 32.88 30.11 31.02 Avg- 31.33 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.6 | Yes |
| New West inlet (OCU11) | 0.000 0.000 0.000 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 0.10 0.15 0.07 Avg-0.10 | 0.5 | Yes |
| GBT Plant OCU Outlet | 0.000 0.000 0.000 | Unknown | Unknown |