### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 18th October 2022 |  |
| --- | --- |
| Attendees: Mr L. Phillips (L.B. Hounslow) and Mr Emma Mcdonald (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty clean. All Hoppers full and need draining. Tank 1B – Tank empty around 50% of tank covered by grit and requires further flushing. All hoppers were full and needed draining. Tank 2A – Tank empty around 20% of tank covered by grit the tank requires further flushing. All hoppers were full and require draining. Tank 2B – Tank empty around 50% of tank covered by grit requires further flushing – All Hoppers were full and require draining. Tank 3A – Tank empty around 75% of tank covered by thick grit and sludge tank requires further flushing. All Hoppers were full and require draining. Tank 3B – Tank backfilling around 60% of Tank and all Hoppers covered – requires draining. Around. 20% of remainder of tank covered by grit the tank requires further flushing. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty and flushed clean. All Hoppers full and require draining. Tank 6B – Tank empty clean. All Hoppers full and need draining. Tank 7A – Returing Amajets in full operation. Tank 7B – Tank empty recently returned around 75% of tank covered by thick covering of grit tank requires further flushing. All Hoppers containing quantity of grit - requires flushing/removal (shallow hoppers). Tank 8A – Tank backfilling around 60% of tank and all hoppers covered requires draining. Remainder of Tank clean. Tank 8B – Tank backfilling around 60% of tank and all Hoppers covered hoppers require draining. Remainder of tank completely covered by grit and sludge tank requires further flushing. Feed Channel - The level of effluent in both feed channels was approximately 30% capacity. |  |
| Complaints The Council received no complaints by email from MRAG in the preceding week. Thames Water controller advised that they had received no direct complaints in the preceding week. The Council directly received 0 complaints by email in the preceding week: Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; 0.005; ppm; 14:06. Monitor 2; 0.002; ppm; 14:06. Monitor 3; 0.005; ppm; 14:06. Monitor 4; 0.006; ppm; 14:06. Monitor 5; 0.003; ppm; 14:06. Monitor 6; 0.004; ppm; 14:06. Monitor 7; 0.004; ppm; 14:06. Monitor 8; 0.006; ppm; 14:06. Monitor 9; 0.005; ppm; 14:06. Monitor 10; 0.006; ppm; 14:06. Monitor 11; 0.007; ppm; 14:06. Monitor 12; 0.007; ppm; 14:06. Monitor 13; 0.006; ppm; 14:06. Wind Speed; 0.363; mph; 14:06. Wind Direction; 109.763; 14:06. |  |
| Odour Log (Thames): Wednesday 12th October 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. Thursday 13th October 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 spiked at 23:40 – 23:53max 0.022ppm and at 20:23 – 20:38 max 0.020ppm. Operational issues / causes observed. OCU11 vent stack reading high. Actions Taken. Reported via midnight sheet. Friday 14th October 2022 DAY SHIFT Temp. Warm. Weather. Cloudy. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 0.024 03:08 – 04:08. Operational issues / causes observed. OCU11 high ppm on outlet stack. Actions taken. Blank. Saturday 15th October 2022 DAY SHIFT Temp. Warm. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. Sunday 16th October 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. OCU11 stack outlet reading over double what it should be. Actions Taken. Blank. Monday 17th October 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/Patch clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM4 0.0016 3:43 – 3:57. OM10 0.023 1:21 – 1:52. Operational issues / causes observed. OCU11 high ppm outlet vent flare stack running. Actions Taken. Blank. Tuesday 18th October 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Cloudy. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 12/10/2022; 0; 572; 444; 1016; 784; 1800. 14/10/2022; 20; 389; 595; 1004; 784; 1788. 17/10/2022; 0; 656; 595; 1251; 936; 2187. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 6 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 7 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 8 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 9 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 10 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 11 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 12 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 13 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 18 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 19 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 20 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. |  |
| GENERAL Large sludge spill from break in pipe servicing mobile screeners located at entrance to Digesters – area requires clean-up and flushing. Ongoing water leak from plant located at rear of Pasteurisation Plant. Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge Total Imports in preceding seven days = 2071.61m³. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. Tanks 71 & 73 currently out of service and undergoing complete overhaul – Contractors on site. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E No issues. Pasteurisation Plant Streams 1,2 6, and 11 out of service. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) covered with tarpaulin & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. 1x 10-Yard enclosed Rag skip in lower Service Road at front of Power House. 1x open container General Waste skip in Service Road at rear of Pasteurisation Plant. |  |

Odour Control Unit (OCU) performance monitoring – 17/10/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.228 0.224 0.217 | 0.05 | yes |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.129 0.120 0.120 | 0.6 | Yes |
| Transfer PS inlet | 0.579 0.604 0.609 | Unknown | Unknown |
| Transfer PS outlet | 0.025 0.020 0.018 | 0.5 | Yes |
| New West inlet (OCU11) | 0.458 0.446 0.441 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 4.352 4.431 4.230 | 0.5 | yes |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |