### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 11th October 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders and Mr Kumail Haider (L.B. Hounslow) and Mr Ed Hutton (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – All Hoppers full with complete covering of algae - requires draining/over-pumping. Tank 1B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 full and Hopper 2 approx. 75% full with complete covering of algae - requires draining/over-pumping. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 75% full & Hoppers 2 & 3 approx. 25% full with complete covering of algae - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 60% full with complete covering of algae - requires draining/over-pumping. Tank 3A – Tank empty – Approx. 75% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers approx. 75% full with thick crust of sludge - requires draining/over-pumping. Tank 3B – Tank backfilling – approx. 60% of Tank and all Hoppers covered – requires draining/over-pumping. – Approx. 20% of remainder of tank covered by grit and sludge – requires further flushing. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty and flushed clean – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 20% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 7A – Tank in use – no Amajets in use – Tank completely covered with algae. Tank 7B – Tank empty – recently returned – Approx. 75% of tank covered by thick covering of grit and sludge – requires further flushing – All Hoppers containing quantity of grit - requires flushing/removal. Tank 8A – Tank backfilling – approx. 60% of Tank and all Hoppers covered – requires draining/over-pumping. Remainder of Tank clean. Tank 8B – Tank backfilling – approx. 60% of Tank and all Hoppers covered – requires draining/over-pumping. – remainder of tank completely covered by grit and sludge – requires further flushing. Feed Channel - The level of effluent in both feed channels was approximately 30% capacity. |  |
| Complaints The Council received no complaints by email from MRAG in the preceding week. Thames Water controller advised that they had received no direct complaints in the preceding week. The Council directly received three complaints by email in the preceding week: 05/10/22 (00:20) from the area of Sussex Avenue – historic trace data checked for OMU’s in vicinity: OMU’s 1, 2 & 3 = .003. Wind= 228° Speed = 5.4mph 07/10/22 (09:27) from the area of London Road – historic trace data checked for OMU’s in vicinity: OMU1 = .003, OMU2 = .002 & OMU3 = .000, Wind = 223° Speed = 4.7mph 09/10/22 (18.54) from the area of Sussex Avenue – historic trace data checked for OMU’s in vicinity: OMU1 = .004, OMU2 = .002 & OMU3 = .000, Wind = 199° Speed = 4.1mph Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:08. Monitor 2; .001; ppm; 13:08. Monitor 3; .000; ppm; 13:08. Monitor 4; .005; ppm; 13:08. Monitor 5; .000; ppm; 13:08. Monitor 6; .003; ppm; 13:08. Monitor 7; .000; ppm; 13:08. Monitor 8; .005; ppm; 13:08. Monitor 9; .004; ppm; 13:08. Monitor 10; .005; ppm; 13:08. Monitor 11; .004; ppm; 13:08. Monitor 12; .005; ppm; 13:08. Monitor 13; .004; ppm; 13:08. Wind Speed; 0.2; mph; 13:08. Wind Direction; 292°; 13:08. |  |
| Odour Log (Thames): Wednesday 5th October 2022: AM – Cool – Rain with Sunny spells. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes No data. Actions: No data. Thursday 6th October 2022: AM – Warm – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data Actions: No data. Friday 7th October 2022: AM – warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Rain. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Saturday 8th October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cold – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 @ 01:09 & 04:39 max 0.029ppm.” Operational Issues/Causes: “OCU 11 showing HI on outlet stack.” Actions: “Area checked.” Sunday 9th October 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM3 spiked at 08:05-08:40 max 0.029ppm.” Operational Issues/Causes: “OCU No.11 vent stack reading high.” Actions: “Reported.” PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 spike 00:24-00:36 max .007ppm.” Operational Issues/Causes: No data. Actions: No data. Monday 10th October 2022: AM – Cool – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 11th October 2022: AM – Cool – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: ”No issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 spiked at 04:07-05:08 max 0.037ppm.” Operational Issues/Causes “OCU No.11 vent stack reading high.” Actions: “Reported.” # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 10/10/22; 0; 267; 534 (TW figure = 533); 801; 152; 953 (TW figure = 952). |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 2ft below coping stones - Seal weak and bubbling. Digester 6 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. Digester 7 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas – Tank bubbling vigorously with ongoing spill – requires clean-up and anti-foam. Digester 8 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 9 - In use – seal level approx. 18” below coping stones – Seal weak and bubbling. Digester 10 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling – Bell height high requiring draw down of Biogas - Tank bubbling vigorously with ongoing spill – requires clean-up and anti-foam. Digester 11 - In use – seal level approx. 3ft below coping stones – Seal weak and bubbling. Digester 12 - In use – seal level approx. 2ft below coping stones – Seal weak and bubbling. Digester 13 - In use – seal level approx. 2ft below coping stones - Seal weak and bubbling. Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 2ft below coping stones - Seal weak and bubbling. Digester 18 – In use – seal level approx. 4ft below coping stones - Seal weak and bubbling. Digester 19 – In use – seal level approx. 18” below coping stones - Seal weak and bubbling. Digester 20 - In use – seal level approx. 3ft below coping stones - Seal weak and bubbling. |  |
| GENERAL Large sludge spill from break in pipe servicing mobile screeners located at entrance to Digesters – area requires clean-up and flushing. Ongoing water leak from plant located at rear of Pasteurisation Plant. Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge Total Imports in preceding seven days = 2122m³. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. Tanks 71 & 73 currently out of service and undergoing complete overhaul – Contractors on site. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E No issues. Pasteurisation Plant Streams 1,2 and 6 out of service. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) covered with tarpaulin & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. 1x 10-Yard enclosed Rag skip in lower Service Road at front of Power House. 1x open container General Waste skip in Service Road at rear of Pasteurisation Plant. |  |

Odour Control Unit (OCU) performance monitoring – 10/10/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.196 0.135 0.128 | 0.2 | Yes |
| East OCU | 0.225 0.233 0.229 | 0.05 | No |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.00 0.00 0.00 | 0.6 | Yes |
| Transfer PS inlet | 1.229 1.169 1.057 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.5 | Yes |
| New West inlet (OCU11) | 0.458 0.446 0.441 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 3.339 3.193 3.278 | 0.5 | No |
| GBT Plant OCU Outlet | 0.0298 0.0212 0.0143 | Unknown | Unknown |