### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 27th September 2022 |  |
| --- | --- |
| Attendees: Mr L. Phillips & K. Haider (L.B. Hounslow) and Miss Emma McDonald & Lena Wallin (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and clean. All Hoppers were full and require draining. Tank 1B – Tank empty around 50% of tank is covered by grit. The tank requires further flushing. All hoppers were full and require draining. Tank 2A – Tank empty around 20% of tank covered by grit. Tank requires further flushing. Hoppers 1 and 2 were full and required draining. Hopper 3 had been drained to its lowest point. Tank 2B – Tank empty around 50% of tank covered by grit. Tank requires further flushing. All hoppers were full and required draining. Tank 3A – Tank empty – around 60% of tank covered by thick covering of sludge. Tank requires further flushing. All Hoppers were full and required draining. Tank 3B – Tank backfilling around 60% of Tank and all Hoppers covered – requires draining. Around 20% of remainder of tank covered by sludge and requires further flushing. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty and clean. All hoppers full and need draining. Tank 6B – Tank empty around 20% of tank covered by thick covering of grit and tank requires further flushing. All Hoppers full and need draining. Tank 7A – Tank in use – No Amajets in use. Tank 7B – Tank empty around 80% of tank covered by thick covering of sludge tank requires further flushing. All Hoppers containing quantity of grit requires flushing/removal. Tank 8A – Tank backfilling around 60% of Tank and all Hoppers covered – requires draining. Remainder of Tank clean. Tank 8B – Tank backfilling around 40% of Tank and all Hoppers covered tank requires draining. Remainder of tank completely covered by grit and sludge – requires further flushing. Feed Channel - The level of effluent in both feed channels was approximately 30% capacity. |  |
| Complaints The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; 0.004; ppm; 14:21. Monitor 2; 0.001; ppm; 14:21. Monitor 3; 0.003; ppm; 14:21. Monitor 4; 0.006; ppm; 14:21. Monitor 5; 0.000; ppm; 14:21. Monitor 6; 0.003; ppm; 14:21. Monitor 7; 0.000; ppm; 14:21. Monitor 8; 0.007; ppm; 14:21. Monitor 9; 0.000; ppm; 14:21. Monitor 10; 0.004; ppm; 14:21. Monitor 11; 0.004; ppm; 14:21. Monitor 12; 0.004; ppm; 14:21. Monitor 13; 0.004; ppm; 14:21. Wind Speed; 4.401; mph; 14:21. Wind Direction; 281.931; 14:21. |  |
| Odour Log (Thames): Wednesday 21st September 2022 DAY SHIFT Temp. Warm. Weather. Cloudy W/ sunny spells. Odour Readings. All OMU’s in operation. Time: 17:30 Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No issues. Operational issues / causes observed. Blank. Actions Taken. Blank. Thursday 22nd September 2022 DAY SHIFT Temp. Warm. Weather. Sunny w/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. Friday 23rd September 2022 DAY SHIFT Temp. Warm. Weather. Rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. Saturday 24th September 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. Sunday 25th September 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank Actions Taken. Blank. Monday 26th September 2022 DAY SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM8 spiked at 19:09 – 19:21 but less than 15 mins duration. 20:58 – 21:09 but less than 15 mins and 02:55 – 03:11 max 0.018ppm. Operational issues / causes observed. There was a PAS type of odour on the breeze, but no obvious sources found. Actions Taken. Blank. Tuesday 27th September 2022 DAY SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issue found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM8 0.019 18:11 – 18:25. Operational issues / causes observed. Some odour from PAS but no obvious source. Actions Taken. Blank.. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 21/09/2022; 40; 38; 267; 345; 1088; 1433. 23/09/2022; 78; 886; 122; 1086; 1240; 2326. 26/09/2022; 40; 450; 412; 912; 936; 1838. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Was in service and had a weak sloppy seal. Clear sign of a previous spill which had dried. Digester 6 - Was in service had good seal. There was no sign of recent spillage. Digester 7 - was in service weak sloppy seal – No evidence of recent spillage. Digester 8 - Was in service weak sloppy seal – No evidence of recent spillage. Bell height high requiring draw down of Biogas. Digester 9 - was in service weak sloppy seal – No evidence of recent spillage. Digester 10 - Was in service had good seal. There was no sign of recent spillage. Digester 11 - Was in service and had a weak sloppy seal. Clear sign of a previous spill which had dried. Digester 12 - Was in service weak sloppy seal – No evidence of recent spillage. Digester 13 - Was in service weak sloppy seal – No evidence of recent spillage. Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - Was in service had good seal. There was no sign of recent spillage. Digester 18 – Was in service weak sloppy seal – No evidence of recent spillage. Digester 19 – was in service weak sloppy seal – No evidence of recent spillage. Digester 20 - Was in service weak sloppy seal – No evidence of recent spillage. |  |
| GENERAL Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge One Hundred and Five (105) Imports in preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. Tanks 71 & 73 currently out of service and undergoing complete overhaul – Contractors on site. FST’s 61-64 drained down – quantity of sludge at bottom of each – significant localised odour – requires removal. East Side Raw Sludge Screen House Doors open at time of inspection – Contractors on site undertaking maintenance. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E No issues. Pasteurisation Plant No Data. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) covered with tarpaulin & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. |  |

Odour Control Unit (OCU) performance monitoring – 26/09/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.00 0.00 0.00 | 0.05 | No |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | No |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.081 0.149 0.135 | 0.6 | Yes |
| Transfer PS inlet | 0.078 0.063 0.065 | Unknown | Unknown |
| Transfer PS outlet | 0.007 0.006 0.003 | 0.5 | Yes |
| New West inlet (OCU11) | 0.00 0.00 0.00 | 0.5 | No |
| Pasteurisation Plant (OCU12) | 1.179 1.848 1.855 | 0.5 | No |
| GBT Plant OCU Outlet | 0.021 0.019 0.011 | Unknown | Unknown |