### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 06th September 2022 |  |
| --- | --- |
| Attendees: Mr L. Phillips (L.B. Hounslow) and Miss Roxanna Denny (Thames Water) and Miss Emma McDonald (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and clean – All hoppers full and need draining. Tank 1B – Tank empty Around 50% of the tank is covered in grit and the tank needs flushing. Hoppers 1 and 3 are full and need draining. Hopper 2 has been drained to lowest point. Tank 2A – Tank empty around 20% of tank covered by grit and the tank needs flushing. Hoppers 1 and 2 are full and need draining. Hopper 3 has been drained to lowest point. Tank 2B – Tank empty – around 50% of tank covered by grit tank requires further flushing. All Hoppers are full and need draining. Tank 3A – Tank empty – around. 80% of tank covered by grit the tank requires further flushing. All Hoppers are full and need draining. Tank 3B – Tank empty – around 90% of tank covered by grit the tank requires further flushing. All hoppers full and need draining. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty around 20% of tank covered by grit the requires further flushing – All Hoppers full and require draining. Tank 6B – Tank empty around 20% of tank covered by grit the requires further flushing – All Hoppers full and require draining. Tank 7A – returning Amajes in operation. Tank 7B – Returning Amajets in operation. Tank 8A – Tank backfilling – around 20% of Tank and all Hoppers covered – requires draining/over-pumping. Remainder of Tank clean. Tank 8B – Tank empty – 100% of tank covered by sludge tank requires further flushing. All Hoppers full and require draining. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - -noticeable fat deposits on surface - no local odours. Sluice gate has large fatty sludge deposits across surface. |  |
| Complaints The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection. Monitor 1; 0.000; ppm; 14:10. Monitor 2; 0.001; ppm; 14:11. Monitor 3; 0.000; ppm; 14:11. Monitor 4; 0.000; ppm; 14:11. Monitor 5; 0.000; ppm; 14:11. Monitor 6; 0.000; ppm; 14:11. Monitor 7; 0.006; ppm; 14:11. Monitor 8; 0.005; ppm; 14:11. Monitor 9; 0.000; ppm; 14:11. Monitor 10; 0.004; ppm; 14:11. Monitor 11; 0.005; ppm; 14:11. Monitor 12; 0.000; ppm; 14:11. Monitor 13; 0.003; ppm; 14:11. Wind Speed; 1.113; mph; 14:11. Wind Direction; 201.408; 14:11. |  |
| Odour Log (Thames): Wednesday 31st August 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. OM3 0.018 7:51 – 8:06. Operational issues / causes observed. Ocu11 stack outlet reading double what it should be. Actions Taken. Area checked. NIGHT SHIFT Temp. Warm. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 spiked at 20:36 – 20:51 max 0.020ppm and again at 00:07 – 00:21 but less than 15 minutes duration. Operational issues / causes observed. OCU11stack outlet reading over double what it should be. Actions Taken. Blank. Thursday 1st September 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Patchy Rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 spiked at 19:52 – 20:07 max 0.017ppm and at 00:20 – 00:36 max 0.017ppm. Operational issues / causes observed. OCU11 stack outlet reading over double what it should be. Actions Taken. Blank. Friday 2nd September 2022 DAY SHIFT Temp. Warm. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. Saturday 3rd September 2022 DAY SHIFT Temp. Warm. Weather. Cloudy. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Cloudy. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. Sunday 4th September 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 0.018 22:37 – 23:07. Operational issues / causes observed. OCU11 stack outlet reading over double what it should be. Actions Taken. Blank. Monday 5th September 2022 DAY SHIFT Temp. Warm. Weather. Rain W/ Sunny spells. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 0.031 23:35 – 23:51. 0.026 4:05 – 4:21. 0.019 4:51 – 5:05. Operational issues / causes observed. Ocu11 stack outlet reading over double what it should be high flows. Actions Taken. Blank. Tuesday 06th September 2022 DAY SHIFT Temp. Cool. Weather. Rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. OM5 0.015ppm at 05:22 less than 15 minutes duration. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. No sources found. Actions Taken. Blank. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 31/08/2022; 59; 328; 0; 387; 1088; 1475. 02/09/2022; 20; 595; 0; 615; 608; 1223. 05/09/2022; 39; 473; 473; 985; 608; 1593. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 6 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 7 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 8 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 9 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 10 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 11 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 12 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 13 - In use – seal level approx. 18” below coping stones - seal weak and bubbling. Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 18 – was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 19 – was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 20 - was in service and had a weak sloppy seal. There was no sign of recent spillage. |  |
| GENERAL Large pile of rag by skips at front of Sludge Screening House half covered by tarpaulin requires removal and as an interim complete covering whilst awaiting skip. Sludge Screening House 2x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge No data provided. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 23 – requires jetting. Pasteurisation Plant No data provided. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) uncovered & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. 1x Container Skip (empty) by Circular PST’s 9-12. |  |

Odour Control Unit (OCU) performance monitoring – 05/09/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.102 0.101 0.100 Ave:0.101 | 0.2 | Yes |
| East OCU | 0.238 0.261 0.246 Ave:0.248 | 0.05 | No |
| West inlet OCU | 0.098 0.073 0.069 Ave:0.08 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.032 0.031 0.031 Ave:0.031 | 0.6 | Yes |
| Transfer PS inlet | 0.685 0.716 0.644 | Unknown | Unknown |
| Transfer PS outlet | 0.109 0.112 0.110 Ave:0.110 | 0.5 | Yes |
| New West inlet (OCU11) | 0.610 0.612 0.614 Ave:0.612 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 2.909 3.098 3.006 Ave:3.004 | 0.5 | No |
| GBT Plant OCU Outlet | 0.028 0.026 0.013 Ave: 0.022 | Unknown | Unknown |