### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 31st August 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Miss Caitlin Simmonds (Thames Water) and Miss Emma McDonald (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – All Hoppers approx. 80% full with thick crust of sludge - requires draining/over-pumping. Tank 1B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers drained down and empty. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 30% full with thick crust of sludge - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 40% full with thick crust of sludge - requires draining/over-pumping. Tank 3A – Tank empty – Approx. 75% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 60% full with thick crust of sludge - requires draining/over-pumping. Tank 3B – Tank empty – Approx. 80% of tank covered by grit and sludge – requires further flushing – All Hoppers full with thick crust of sludge - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 50% full - requires draining/over-pumping. Tank 7A – Tank empty - approx. 90% of Tank covered grit and sludge - requires further flushing – All Hoppers full with thick crust of sludge - requires draining/over-pumping. Tank 7B – Tank empty - approx. 75% of Tank covered grit and sludge - requires further flushing – All Hoppers full with thick crust of sludge - requires draining/over-pumping. Tank 8A – Tank backfilling – approx. 25% of Tank and all Hoppers covered – requires draining/over-pumping. Remainder of Tank clean. Tank 8B – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 85% full with thick crust of sludge - requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - -noticeable fat deposits on surface - no local odours. Sluice gate has large fatty sludge deposits across surface. |  |
| Complaints The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:13. Monitor 2; .002; ppm; 13:13. Monitor 3; .008; ppm; 13:13. Monitor 4; .004; ppm; 13:13. Monitor 5; .004; ppm; 13:13. Monitor 6; .003; ppm; 13:13. Monitor 7; .000; ppm; 13:13. Monitor 8; .004; ppm; 13:13. Monitor 9; .003; ppm; 13:13. Monitor 10; .004; ppm; 13:13. Monitor 11; .006; ppm; 13:13. Monitor 12; .004; ppm; 13:13. Monitor 13; .005; ppm; 13:13. Wind Speed; 7.6; mph; 13:13. Wind Direction; 28.5°; 13:13. |  |
| Odour Log (Thames): Wednesday 24th August 2022: AM – Hot – Sunny with Patch Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Rain Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes No data. Actions: No data. Thursday 25th August 2022: AM – Warm – Rain. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Cool – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Friday 26th August 2022: AM – Hot – Sunny. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Saturday 27th August 2022: AM – Hot – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: “RSHT Spill.” Actions: “Day Works to clean-up.” Sunday 28th August 2022: AM – Hot – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM3 spiked at 08:05 - 08:20 max 0.019ppm.” Operational Issues/Causes: “OCU 11 Stack outlet reading over double what it should be.” Actions: “Put in Defect book.” PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 spiked @ 21:52 – 23:04 max 0.018ppm.” Operational Issues/Causes: “OCU 11 Stack outlet reading over double what it should be.” Actions: “Area checked.” Monday 29th August 2022: AM – Warm – Sunny with Patch Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 30th August 2022: AM – Warm – Overcast Night (?). All OMU’s in use. Observations/Complaints: ”OCU 11 Stack Outlet reading over double what it should be.” Operational Issues/Causes: “Area in vicinity of OM3 checked but……?” Actions: No data. PM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM3 0.018 07:51 – 08:06.” Operational Issues/Causes ”OCU 11 Stack Outlet reading over double what it should be.” Actions: “Area checked.” Wednesday 31st August 2022: AM – Warm – Overcast Night (?). All OMU’s in use. Observations/Complaints: “OM3 spiked at 20:36 – 20:51 max 0.020ppm and again at 00:07 – 00:21 but <15 mins duration.” Operational Issues/Causes: ”OCU 11 Stack Outlet reading over double what it should be.” No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 24/08/22; 79; 244; 267; 590; 936; 1526. 26/08/22; 40; 122; 122; 284; 608; 892. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 6” below coping stones - Good seal. Digester 6 - In use – seal level approx. 6” below coping stones – Seal weak and bubbling. Digester 7 - In use – seal level approx. 3ft below coping stones – Good seal. Digester 8 - In use – seal level approx. 3ft below coping stones – Seal weak and bubbling. Digester 9 - In use – seal level approx. 3ft below coping stones – Seal weak and bubbling. Digester 10 - In use – seal level approx. 18” below coping stones – Seal weak and bubbling. Digester 11 - In use – seal level approx. 4ft below coping stones – Seal weak and bubbling. Digester 12 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 18” below coping stones - seal weak and bubbling. Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 18 – In use – seal level approx. 3ft below coping stones – Good seal (stones in use). Digester 19 – In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 2ft below coping stones – seal weak and bubbling. |  |
| GENERAL Large pile of rag by skips at front of Sludge Screening House half covered by tarpaulin requires removal and as an interim complete covering whilst awaiting skip. Sludge Screening House 2x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge Seventy (70) Imports in preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 23 – requires jetting. Pasteurisation Plant Eight (8) streams in use. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) uncovered & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. 1x Container Skip (empty) by Circular PST’s 9-12. |  |

Odour Control Unit (OCU) performance monitoring – 30/08/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.172 0.176 0.170 | 0.05 | No |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.376 0.374 0.370 | 0.6 | Yes |
| Transfer PS inlet | 0.476 0.478 0.486 | Unknown | Unknown |
| Transfer PS outlet | 0.266 0.268 0.269 | 0.5 | Yes |
| New West inlet (OCU11) | 0.468 0.460 0.458 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 3.662 4.558 4.489 | 0.5 | No |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |