### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 16th August 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Miss Caitlin Simmonds (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – Hopper 1 approx. 20% full (in process of being over-pumped), Hoppers 2 & 3 drained down and empty. Tank 1B – Tank empty – Approx. 15% of tank covered by grit and sludge – requires further flushing – All Hoppers drained down and empty. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers drained down and empty. Tank 2B – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 75% full - requires draining/over-pumping. Tank 3A – Tank empty and flushed clean – All Hoppers filled with grit from Tank cleaning exercise – awaiting manual removal. Tank 3B – Tank empty - approx. 10% of Tank covered by grit and sludge - requires draining/over-pumping. Hoppers 1 & 2 approx. 40% full - Hopper 3 approx. 75% full – requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 2 approx. 40% full - Hopper 3 approx. 60% full - requires draining/over-pumping. Tank 6B – Tank empty and flushed clean – All Hoppers full - requires draining/over-pumping. Tank 7A – Tank empty - approx. 90% of Tank covered grit and sludge - requires further flushing – All Hoppers full - requires draining/over-pumping. Tank 7B – Tank backfilling – approx. 50% of Tank covered – remainder covered with grit/sludge – requires further flushing – All Hoppers full - requires draining/over-pumping. Tank 8A – Tank empty and flushed clean – Hoppers 1 & 3 approx. 50% full - Hopper 2 approx. 40% full - requires draining/over-pumping. Tank 8B – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing. All Hoppers approx. 30% full – requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 10% capacity - no local odours. |  |
| Complaints The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:15. Monitor 2; .002; ppm; 13:15. Monitor 3; .000; ppm; 13:15. Monitor 4; .000; ppm; 13:15. Monitor 5; .000; ppm; 13:15. Monitor 6; .000; ppm; 13:15. Monitor 7; .007; ppm; 13:15. Monitor 8; .003; ppm; 13:15. Monitor 9; .000; ppm; 13:15. Monitor 10; .004; ppm; 13:15. Monitor 11; .004; ppm; 13:15. Monitor 12; .000; ppm; 13:15. Monitor 13; .000; ppm; 13:15. Wind Speed; 0.2; mph; 13:15. Wind Direction; 167°; 13:15. |  |
| Odour Log (Thames): Tuesday 9th August 2022: AM – Hot – Sunny. All OMU’s in use. Observations/Complaints: ”No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “OM10 0.018 03:32 - 03:47, 0.016 04:01 – 04:16.” Operational Issues/Causes ”No source found.” Actions: No data Wednesday 10th August 2022: AM – Hot – Sunny. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “OM5 0.028 03:18 – 03:51. OM8 0.019 03:52 – 04:09. OM9 0.015 04:08 – 04:22.” Operational Issues/Causes “Odour from Main Drive.” Actions: No data. Thursday 11th August 2022: AM – Hot – Sunny. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “Multiple spikes from OM’s 3, 5, 10, 11, 12 & 13 throughout shift.” Operational Issues/Causes: “Odour from Main Drive vent, Odour from PAS. OCU11 high discharge of H2S from stack.” Actions: No data. Friday 12th August 2022: AM – Very Hot – Sunny. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Hot – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 spiked at 21:49 – 22:03 and 00:35 – 00:49 but <15 mins duration max 0.018ppm. OM5 spiked between 03:20 – 06:05 max 0.034ppm. OM10 multiple spikes between 03:30 – 06:00 max 0.020ppm. OM11 multiple spikes between 00:34 – 01:05 max 0.021ppm.” Operational Issues/Causes: “Odour at Main Drive man-hole chamber and PAS odour in the air but unable to pinpoint source around the pasteurisation streams.” Actions: No data. Saturday 13th August 2022: AM – Very Hot – Sunny. All OMU’s in use. Observations/Complaints: “OM5 0.019 07:19 – 07:35. ).017 ONGOING – 06:05.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “Multiple spikes from OM5 between 20:18 – now max 0.055ppm. OM3 spiked 20:20 – 20:35 max 0.024ppm. OM’s 9, 10, 11 multiple spikes between…….?” Operational Issues/Causes: “Main Drive manhole cover oderous. OCU No.11 exhaust stack reading is high. Pasteurisation type odour in the breeze.” Actions: “Reported OCU No.11 in defect log. Unable to locate other source of odour.” Sunday 14th August 2022: AM – Very Hot – Sunny. All OMU’s in use. Observations/Complaints: “OM5 0.55 MAX PEAK ongoing – 06:17 0.020 07:04 – 07:20. OM10 0.032 max peak 05:31 – 06:17 0.024 max peak 06:30 – 07:16. OM9 0.026 05:22 – 05:33.” Operational Issues/Causes: “Odour from Main Drive vent. Some odour from PAS – no obvious source.” Actions: No data. PM – Hot – Clear Night. All OMU’s in use. Observations/Complaints: “OM5 spiked at 20:05 – 20:20 max 0.020ppm, 04:50 – 05:05 max 0.021ppm & 03:50 – 04:15 max 0.015ppm. OM10 spiked at 01:45 – 02:03 max 0.028ppm.” Operational Issues/Causes: “Odour coming from manhole cover on Main Drive.” Actions: No data. Monday 15th August 2022: AM – Hot – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Patchy Rain. All OMU’s in use. Observations/Complaints: “OM3 spiked at 22:50 – 00:05 max 0.041ppm. OM11 spiked at 23:05 – 23:30 max 0.025ppm.” Operational Issues/Causes: “OCU 11 Exhaust stack reading high. Odour at Main Drive manhole chamber.” Actions: No data. Tuesday 16th August 2022: AM – Hot – Patchy rain. All OMU’s in use. Observations/Complaints: ”No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Patchy rain. All OMU’s in use. Observations/Complaints: “OM3 spiked at 19:20 – 19:35 & 21:50 – 22:50 max 0.064ppm. OM5 spiked at 22:35 – 22:50 & 00:50 – 10:20 max 0.039 ppm. OM8 spiked at 01:40 – 01:56 max 0.023ppm. OM10 spiked at 01:50 – 02:02 max 0.018ppm.” Operational Issues/Causes “OCU11 Exhaust stack reading high. Odour at Main Drive manhole chamber. “PAS” type odour in breeze.” Actions: No data. Wednesday 17th August 2022: AM – Warm – Rain. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Rain. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes “Storm Tanks full.” Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 12/08/22; 40; 450; 412; 902; 1088; 1990. 15/08/22; 20; 61; 473; 554; 456; 1010. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 3ft below coping stones - Good seal. Digester 6 - In use – seal level approx. 4ft below coping stones – Good seal. Digester 7 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 8 - In use – seal level approx. 4ft below coping stones – Good seal. Digester 9 - In use – seal level approx. 3ft below coping stones – Good seal. Digester 10 - In use – seal level approx. 4ft below coping stones – Good seal. Digester 11 - In use – seal level approx. 3ft below coping stones – Good seal. Digester 12 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Digester 14 - In use – seal level approx. 4ft below coping stones – Good seal. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 2ft below coping stones – seal weak and bubbling. Digester 18 – In use – seal level approx. 4ft below coping stones – Good seal (stones in use). Digester 19 – In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. |  |
| GENERAL Sludge Screening House 2x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge Ninety (90) Imports in preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. Pasteurisation Plant Nine (9) streams in use. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) uncovered & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. |  |

Odour Control Unit (OCU) performance monitoring – 15/08/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.12 0.13 0.17 | 0.05 | No |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.39 0.38 0.35 | 0.6 | Yes |
| Transfer PS inlet | 2.453 2.258 2.856 | Unknown | Unknown |
| Transfer PS outlet | 0.145 0.148 0.150 | 0.5 | Yes |
| New West inlet (OCU11) | 0.437 0.436 0.434 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 4.196 4.402 4.358 | 0.5 | No |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |