### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 09th August 2022 |  |
| --- | --- |
| Attendees: Mr L. Phillips (L.B. Hounslow) and Miss Caitlin Simmonds (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty clean. All hoppers drained down to lowest point. Tank 1B – Tank empty around 20% of tank covered by grit tank needs flushing. All Hoppers drained down to lowest point. Tank 2A – Tank empty around 20% of tank covered by grit tank needs flushing. All Hoppers drained down to lowest point. Tank 2B – Tank empty – around 10%of of tank filled with grit tank needs flushing. Hopper 1 is full and needs draining. Hoppers 2 and 3 are drained down to lowest point. Tank 3A – Tank empty and clean. All hoppers are full and need draining. Tank 3B – Tank empty around 10% of Tank covered by grit the tank needs flushing. All hoppers filled with grit and it needs to be removed advised by Thames that this will be done manually. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty and clean. Hoppers 1 and 2 have been drained to lowest point. Hopper 3 is full and needs draining. Tank 6B – Tank empty and clean. Hopers 1 and 2 have been drained to lowest point. Hopper 3 is full and needs draining. Tank 7A – Tank empty 90% of tank covered in dry grit. Tank needs flushing. All hoppers full and need draining. Tank 7B – Tank backfilling – around 50% of Tank is covered in grit. Tank needs flushing. All Hoppers full and need draining. Tank 8A – Tank empty and clean. Hoppers 1 and 2 have been drained to lowest point. Hopper 3 is full and requires draining. Tank 8B – Tank empty around 10% of tank covered by grit. Tank needs flushing. All hoppers drained to lowest point. Feed Channel - The level of effluent in both feed channels was approximately 10% capacity - no local odours. |  |
| Complaints The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; 0.000; ppm; 14:54. Monitor 2; 0.001; ppm; 14:54. Monitor 3; 0.000; ppm; 14:54. Monitor 4; 0.008; ppm; 14:54. Monitor 5; 0.004; ppm; 14:54. Monitor 6; 0.000; ppm; 14:54. Monitor 7; 0.000; ppm; 14:54. Monitor 8; 0.004; ppm; 14:54. Monitor 9; 0.004; ppm; 14:54. Monitor 10; 0.004; ppm; 14:54. Monitor 11; 0.006; ppm; 14:54. Monitor 12; 0.004; ppm; 14.54. Monitor 13; 0.004; ppm; 14:54. Wind Speed; 5.003; mph; 14:54. Wind Direction; 79.469; 14:54. |  |
| Odour Log Wednesday 3rd August 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odours or issue reported. Operational issues / causes observed. Blank. Actions Taken. Blank. Thursday 4th August 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM8 0.015ppm 6:07 – 6:21. 0.022 13:07 – 13:22. Operational issues / causes observed. PAS smelling. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear Night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM8 0.020ppm 22:18 – 23:22. Operational issues / causes observed. No odour identified. Actions Taken. Blank. Friday 5th March 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. Saturday 6th August 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Customer complaint at 21:00Hrs monitor 10 spiked around that time. Peaked at 0.019ppm. Operational issues / causes observed. Digester area checked as well as surrounding areas. Nothing out of the ordinary detected. Digesters not gassing off. Bell height was low as 23 meters. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. Multiple spikes and breaches from OM1, OM3, OM5, OM9, OM10 throughout shift. Operational issues / causes observed. Whole site inspection carried out. Odour identified from main drive manhole cover. No evidence of any sludge spills around PAS or Digesters. OCU11 discharging high odour from stack >1100ppb. Actions taken. Blank. Sunday 7th August 2022 DAY SHIFT Temp. Hot. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM5 0.023ppm 19:04 – 19:19. OM8 0.016ppm 02:09 – 03:08. OM9 0.016ppm 21:08 – 21:34. OM10 0.024ppm 23:03 – 23:03. 0.017ppm 03:31 – 03:47. Operational issues / causes observed. Slight odour from PAS and main drive manhole. Nothing else out of the ordinary found. OCU11 discharging high H25 from stack. Chemical dosing not running. Actions Taken. Blank. Monday 8th March 2022 DAY SHIFT Temp. Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 0.015ppm at 1:50 less than 15 minutes. OM5 0.016ppm at 2:50 less than 15 minutes. OM10 0.020ppm 04:47 less than 15 minutes. Operational issues / causes observed. No odour issues on site. Actions Taken. Blank. Tuesday 9th March 2022 DAY SHIFT Temp. Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM10 0.018 3:32 – 3:47. 0.016 4:01 – 4:16. OM3 0.022 20:50 – 21:04. Operational issues / causes observed. No sources found. Actions Taken. Blank.. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 05/08/22; 40; 450; 473; 963; 936; 1899. 08/08/22; 20; 183; 473; 676; 1240; 1916. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 6 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 7 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 8 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 9 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 10 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 11 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 12 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 13 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 18 – Was in service and good seal. There was no sign of recent spillage. Digester 19 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 20 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. |  |
| GENERAL Sludge Screening House 2x (pedestrian) door open at time of inspection. Roller shutter closed. Imported Sludge Seventy-two (72) Imports in preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. Pasteurisation Plant Nine (9) streams in use. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (partially full) uncovered & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. |  |

Odour Control Unit (OCU) performance monitoring – No data provided

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | No data | No data |
| Main pumping station outlet | No data | No data | No data |
| East OCU | No data | No data | No data |
| West inlet OCU | No data | No data | No data |
| Sludge reception inlet | No data | No data | No data |
| Sludge reception outlet | No data | No data | No data |
| Thickening plant inlet | No data | No data | No data |
| Thickening plant outlet | No data | No data | No data |
| Transfer PS inlet | No data | No data | No data |
| Transfer PS outlet | No data | No data | No data |
| New West inlet (OCU11) | No data | No data | No data |
| Pasteurisation Plant (OCU12) | No data | No data | No data |
| GBT Plant OCU Outlet | No data | No data | No data |