### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 26th July 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Mr Neil Bristow (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – Hopper 1 approx. 20% full (in process of being over-pumped), Hoppers 2 & 3 drained down and empty. Tank 1B – Tank empty – Approx. 40% of tank covered by grit and sludge – requires further flushing – All Hoppers drained down and empty. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers drained down and empty. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 40% full – thick crust on surface - requires draining/over-pumping - Hoppers 2 & 3 drained down and empty. Tank 3A – Tank empty – 10% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 80% full – thick crust on surface – requires draining/over-pumping. Tank 3B – Tank empty - approx. 75% of Tank covered by grit and sludge - requires draining/over-pumping. Hopper 1 in process of being over-pumped - Hoppers 2 & 3 approx. 30% full – requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 40% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 10% of tank covered by grit and sludge – Hoppers 1 & 2 drained down and empty, Hopper 3 approx. 40% full - requires draining/over-pumping. Tank 7A – Tank back-filling - approx. 75% of Tank covered by stagnant water – Hoppers covered by stagnant water – remainder of Tank covered by grit and sludge - requires flushing and draining/over-pumping. Tank 7B – Tank back-filling - approx. 75% of Tank covered by stagnant water – Hoppers covered by stagnant water – remainder of Tank covered by grit and sludge - requires flushing and draining/over-pumping. Tank 8A – Tank empty and flushed clean – All Hoppers drained down and empty. Tank 8B – Tank empty – Approx. 30% of tank covered by grit and sludge – requires further flushing. All Hoppers drained down and empty. Feed Channel - The level of effluent in both feed channels was approximately 10% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:42. Monitor 2; .001; ppm; 13:42. Monitor 3; .000; ppm; 13:42. Monitor 4; .005; ppm; 13:42. Monitor 5; .000; ppm; 13:42. Monitor 6; .003; ppm; 13:42. Monitor 7; .000; ppm; 13:42. Monitor 8; .005; ppm; 13:42. Monitor 9; .003; ppm; 13:42. Monitor 10; .003; ppm; 13:42. Monitor 11; .004; ppm; 13:42. Monitor 12; .004; ppm; 13:42. Monitor 13; .000; ppm; 13:42. Wind Speed; 0.2; mph; 13:42. Wind Direction; 9.2°; 13:42. |  |
| Odour Log (Thames): No data # Sludge Dip Records No data Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 2ft below coping stones - Good seal. Digester 6 - In use – seal level approx. 4ft below coping stones – Good seal. Digester 7 - In use – seal level approx. 4ft below coping stones – Good seal. Digester 8 - In use – seal level approx. 4ft below coping stones – Good seal. Digester 9 - In use – seal level approx. 3ft below coping stones – Good seal. Digester 10 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 11 - In use – seal level approx. 2ft below coping stones – Good seal. Digester 12 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 14 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 5ft below coping stones – seal weak and bubbling. Digester 18 – In use – seal level approx. 4ft below coping stones – Good seal (stones in use). Digester 19 – In use – seal level approx. 5ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. |  |
| GENERAL Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. Quantity of rag on swing bridge at rear of Screen House requires removal. Imported Sludge No data. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection. Contractors on site undertaking maintenance. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. Pasteurisation Plant No data. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (full) uncovered, 1x open container skip – General Waste (full) & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. |  |

Odour Control Unit (OCU) performance monitoring – No data

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown |  |
| Main pumping station outlet | No data | 0.2 |  |
| East OCU | No data | 0.05 |  |
| West inlet OCU | No data | 0.05 |  |
| Sludge reception inlet | No data | Unknown |  |
| Sludge reception outlet | No data | 0.8 |  |
| Thickening plant inlet | No data | Unknown |  |
| Thickening plant outlet | No data | 0.6 |  |
| Transfer PS inlet | No data | Unknown |  |
| Transfer PS outlet | No data | 0.5 |  |
| New West inlet (OCU11) | No data | 0.5 |  |
| Pasteurisation Plant (OCU12) | No data | 0.5 |  |
| GBT Plant OCU Outlet | No data | Unknown |  |

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown

Unknown