### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 19th July 2022 |  |
| --- | --- |
| Attendees: Mr L. Phillips (L.B. Hounslow) and Mr Neil Bristow (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A - Was empty and clean. All hoppers had been drained to lowest point. Tank 1B - Was empty 50% of tank covered by dry grit. Tank needs flushing. All Hoppers drained down to lowest point. Tank 2A - Was empty around 40% of tank covered by dry grit. Tank needs flushing. All Hoppers drained down to lowest point. Tank 2B - Was empty around 50% of tank covered by grit therefore tank requires further flushing. Hopper 1 was full and needed draining. Hoppers 2 and 3 were drained to lowest point. Tank 3A - Was empty around 20% of tank covered by grit tank requires further flushing. All Hoppers were full and needed draining. Tank 3B - Was Empty around 80% of the tank covered by grit tank requires flushing. Hopper 1 was 50% full and required draining - Hoppers 2 & 3 had been drained to lowest point. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A - Was Empty slight amount of dry grit in tank. All hoppers were full and needed draining. Tank 6B - Was Empty slight grit in tank. Hoppers 1 and 2 drained to lowest point. Hopper 3 50% full and needed draining. Tank 7A - Tank back-filling around 60% of Tank covered by stagnant water. Hoppers covered by stagnant water remainder of Tank covered by grit and sludge - requires flushing and draining. Tank 7B - Tank back-filling - approx. 60% of Tank covered by stagnant water. Hoppers covered by stagnant water remainder of Tank covered by grit and sludge requires flushing and draining. Tank 8A - Was empty and clean. All Hoppers drained down to lowest point. Tank 8B - Was Empty around 30% of tank covered by grit and requires further flushing. All Hoppers drained down to lowest point. Feed Channel - The level of effluent in both feed channels was approximately 10% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; 0.000; ppm; 13:06. Monitor 2; 0.001; ppm; 13:06. Monitor 3; 0.000; ppm; 13:06. Monitor 4; 0.005; ppm; 13:06. Monitor 5; 0.000; ppm; 13:06. Monitor 6; 0.003; ppm; 13:07. Monitor 7; 0.000; ppm; 13:07. Monitor 8; 0.005; ppm; 13:07. Monitor 9; 0.003; ppm; 13:07. Monitor 10; 0.003; ppm; 13:07. Monitor 11; 0.004; ppm; 13:07. Monitor 12; 0.004; ppm; 13:07. Monitor 13; 0.000; ppm; 13:07. Wind Speed; 7.132; mph; 13:07. Wind Direction; 156.650; Deg; 13:07. |  |
| Odour Log (Thames): Tuesday 12th July 2022 DAY SHIFT Temp. Hot. Weather. Sunny w/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. OM5 06:18 – 06:47 and 13.03 – 13:17max 0.028ppm. Operational issues / causes observed. Vent on main drive. Actions Taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM5 0.020ppm 21.36 – 22:34. Operational issues / causes observed. No odour detected. Actions Taken. Blank. Wednesday 13th July 2022 DAY SHIFT Temp. Hot. Weather. Sunny w/ Patchy clouds. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. Thursday 14th July 2022 DAY SHIFT Temp. Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. MRAG Customer complaint received via WOCC at 15:15. Operational issues / causes observed. No odours found or reported. Actions taken. Checked for odour spikes and walked the site no abnormal odours found. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. Friday 15th July 2022 DAY SHIFT Temp. Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. OM4 spiked at 12:06 – 122:max 0.018ppm. Operational issues / causes observed. Area in vicinity of OM4 checked and no odours found. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. Saturday 16th July 2022 DAY SHIFT Temp. Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 spiking from 02:33 until 05:30max Operational issues / causes observed. OCU11showing hi at 924pbb. Actions Taken. Area checked no odours found. Sunday 17th July 2022 DAY SHIFT Temp. Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Warm. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. Lots of odours showing after 24:00. Operational issues / causes observed. Monitors 3,4,5,8,11,12, all showing odours vent on main drive. Actions Taken. OCU checked and site inspected digesters not blowing seals gas low. Monday 18th July 2022 DAY SHIFT Temp. Very hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. 3,8,9,10,11 showing odours 05:30 – 5:52. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Hot. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. Site wide odours after power failure. Operational issues / causes observed. All OCU’S failed. Actions Taken. All OCU’S reset.. Tuesday 19th July 2022 DAY SHIFT Temp. Very Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Hot. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 15/07/2022; 137; 389; 61; 587; 456; 1043. 18/07/2022; 166; 305; 61; 532; 936; 1468. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 6 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 7 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 8 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 9 – Was in service had good seal. There was no sign of recent spillage. Digester 10 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 11 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 12 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 13 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 14 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 18 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 19 – Was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 20 - Was in service and had a weak sloppy seal. There was no sign of recent spillage. |  |
| GENERAL Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. Quantity of rag on swing bridge at rear of Screen House requires removal. Imported Sludge No data. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection. Contractors on site undertaking maintenance. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Number 12 drained down. Pasteurisation Plant No data. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (full) uncovered, 1x open container skip – General Waste (full) & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. |  |

Odour Control Unit (OCU) performance monitoring: 20/07/2022

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | Not provided | Unknown | Unknown |
| Main pumping station outlet | 0.00ppm 0.00ppm 0.00ppm | 0.2 | Unknown |
| East OCU | 0.00ppm 0.00ppm 0.00ppm | 0.05 | Yes |
| West inlet OCU | 0.00ppm 0.00ppm 0.00ppm | 0.05 | Yes |
| Sludge reception inlet | Not provided | Unknown | Unknown |
| Sludge reception outlet | Not provided | 0.8 | Unknown |
| Thickening plant inlet | Not provided | Unknown | Unknown |
| Thickening plant outlet | 0.00ppm 0.00ppm 0.00ppm Ave:0.00ppm | 0.6 | Yes |
| New West inlet (OCU 11) | 0.00ppm 0.00ppm 0.00ppm Ave:0.00ppm | 0.5 | No |
| Pasteurization (OCU 12) | 0.00ppm 0.01ppm 0.01ppm Ave:0.00ppm | 0.5 | Yes |
| Transfer PS inlet | 9.77ppm 9.21ppm 8.62ppm Ave:3.066ppm | Unknown | Unknown |
| Transfer PS outlet | 0.00ppm 0.00ppm 0.00ppm | 0.6 | Yes |
| GBT Plant OCU Outlet | 0.00ppm 0.00ppm 0.00ppm | Unknown | Unknown |