### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 28th June 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Ms Caitlin Simmonds (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – Hopper 1 approx. 90% full - thick crust on surface, Hoppers 2 & 3 approx. 40% full – requires draining/over-pumping. Tank 1B – Tank empty – Approx. 40% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 80% full – thick crust on surface - requires draining/over-pumping. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 80% full – thick crust on surface - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hopper 1 full – thick crust on surface - Hoppers 2 & 3 approx. 80% full - requires draining/over-pumping. Tank 3A – Tank empty – 90% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 90% full, Hoppers 2 & 3 approx. 60% full – requires draining/over-pumping. Tank 3B – Tank back-filling and approx. 75% of Tank covered by stagnant water and sludge - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 95% full, Hoppers 2 & 3 approx. 80% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 approx. 90% full, Hopper 2 approx. 25% full - requires draining/over-pumping. Tank 7A – Tank back-filling and Hoppers covered by stagnant water – remainder of Tank covered by grit and sludge - requires flushing and draining/over-pumping. Tank 7B – Tank back-filling and approx. 75% of Tank covered by stagnant water with – remainder of Tank covered by grit and sludge - All Hoppers covered by stagnant water - requires flushing and draining/over-pumping Tank 8A – Tank empty and flushed clean – Hopper 1 approx. 80% full, Hoppers 2 & 3 approx. 50% full - requires draining/over-pumping. Tank 8B – Tank empty – Approx. 30% of tank covered by grit and sludge – requires further flushing. Hoppers 1 & 3 approx. 80% full, Hopper 2 approx. 50% full - requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 10% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .003; ppm; 14:06. Monitor 2; .001; ppm; 14:06. Monitor 3; .004; ppm; 14:06. Monitor 4; .005; ppm; 14:06. Monitor 5; .004; ppm; 14:06. Monitor 6; .005; ppm; 14:06. Monitor 7; .000; ppm; 14:06. Monitor 8; .006; ppm; 14:06. Monitor 9; .005; ppm; 14:06. Monitor 10; .000; ppm; 14:06. Monitor 11; .006; ppm; 14:06. Monitor 12; .005; ppm; 14:06. Monitor 13; .006; ppm; 14:06. Wind Speed; 15.2; mph; 14:06. Wind Direction; 186°; 14:06. |  |
| Odour Log (Thames): Wednesday 22nd June 2022: AM – Hot – Sunny. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “OM5 showing odours from 01:00 on and off max 0.031ppm. OM3 all shift max 0.022.” Operational Issues/Causes “Vent on Main Drive. PST’s 24 & 25 being refreshed.” Actions: No data. Thursday 23rd June 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “OM5 @ 02:09-02:22 Max 0.027ppm.” Operational Issues/Causes: “Vent on Main Drive.” Actions: No data. Friday 24th June 2022: AM – Warm – Sunny with Patch Clouds. All OMU’s in use. Observations/Complaints: “OM5 0.027ppm 10:38-10:54.” Operational Issues/Causes: “Vent on Main Drive.” Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Saturday 25th June 2022: AM – Warm – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Sunday 26th June 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “OM5 0.019ppm 00:09-00:24.” Operational Issues/Causes: “Area checked. No odour identified.” Actions: No data. Monday 27th June 2022: AM – Warm – Patchy Rain. All OMU’s in use. Observations/Complaints: “OM3 spiked at 14:42-14:56 but <15 mins duration max 0.016ppm. OM5 spiked at 13:33-13:53 max 0.016ppm.” Operational Issues/Causes: ”Sight odour in the air appears to be coming from Pasteurisation area.” Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 28th June 2022: AM – Warm – Sunny with patchy Clouds. All OMU’s in use. Observations/Complaints: ”No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes No data. Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 27/06/22; 0; 1068; 618; 1686; 1720; 3406. 28/06/22; 0; 1213; 618; 1831; 760; 2591. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 3ft below coping stones. Tank seal gassing-off significantly – noticeable odour in vicinity. Quantity of rag surrounding tank requiring removal. Digester 6 - In use – seal level approx. 2ft below coping stones – seal full of debris and other extraneous matter that has by-passed screening. Quantity of rag surrounding tank that requires removal. Digester 7 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 8. - In use – seal level approx. 3ft below coping stones - seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 9 - In use – seal level approx. 18” below coping stones – good seal. Digester 10 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling – Bell height high requiring draw down of Biogas. Tank seal gassing-off significantly – noticeable odour in vicinity. Digester 11 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Tank seal gassing-off significantly – noticeable odour in vicinity. Digester 12 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Tank seal gassing-off significantly – noticeable odour in vicinity. Digester 13 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Tank seal gassing-off significantly – noticeable odour in vicinity. Digester 14. - In use – seal level approx. 1ft below coping stones – seal weak and bubbling. Tank gassing-off – noticeable odour in vicinity. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 18 – Out of use. Digester 19 – In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Tank seal gassing-off significantly – noticeable odour in vicinity. Digester 20 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Tank seal gassing-off significantly – noticeable odour in vicinity. |  |
| GENERAL Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter closed. 2x “Screws” clogged with rag require removal/cleansing. Imported Sludge Seventy-five (75) imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Large fat deposits on surface of 9 & 10. Number 12 drained down. Pasteurisation Plant Eight streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste (empty) & 1x 10-Yard Rag skip (covered). 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. |  |

Odour Control Unit (OCU) performance monitoring – 27/06/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Yes |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.00 0.00 0.00 | 0.6 | Yes |
| Transfer PS inlet | 27.07 22.01 20.01 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.5 | Yes |
| New West inlet (OCU11) | 0.00 0.00 0.00 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 0.02 0.01 0.03 | 0.5 | Yes |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |