### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 7th June 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Ms Caitlin Simmonds (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – Hopper 1 approx. 90% full, Hoppers 2 & 3 approx. 40% full – requires draining/over-pumping. Tank 1B – Tank empty – Approx. 40% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 approx. 80% full, Hopper 2 approx. 40% full - requires draining/over-pumping. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 85% full and covered with thick sludge blanket, Hoppers 2 & 3 approx. 60% full - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hopper 1 full with a thick sludge blanket - Hoppers 2 & 3 approx. 80% full - requires draining/over-pumping. Tank 3A – Tank empty – 90% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 90% full, Hoppers 2 & 3 approx. 60% full – requires draining/over-pumping. Tank 3B – Tank back-filling and approx. 75% of Tank covered by stagnant water - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled, were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 95% full, Hoppers 2 & 3 approx. 60% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 approx. 80% full, Hopper 2 approx. 50% full - requires draining/over-pumping. Tank 7A – Tank back-filling and approx. 75% of Tank covered by stagnant water – remainder of Tank covered by grit and sludge - All Hoppers covered by stagnant water - requires flushing and draining/over-pumping. Tank 7B – Tank back-filling and approx. 75% of Tank covered by stagnant water – remainder of Tank covered by grit and sludge - All Hoppers covered by stagnant water - requires flushing and draining/over-pumping Tank 8A – Tank empty and flushed clean – Hopper 1 approx. 80% full, Hoppers 2 & 3 approx. 30% full - requires draining/over-pumping. Tank 8B – Tank empty and flushed clean – All Hoppers full - requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 10% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:13. Monitor 2; .001; ppm; 13:13. Monitor 3; .004; ppm; 13:13. Monitor 4; .004; ppm; 13:13. Monitor 5; .004; ppm; 13:13. Monitor 6; .004; ppm; 13:13. Monitor 7; .000; ppm; 13:13. Monitor 8; .005; ppm; 13:13. Monitor 9; .003; ppm; 13:13. Monitor 10; .003; ppm; 13:13. Monitor 11; .005; ppm; 13:13. Monitor 12; .005; ppm; 13:13. Monitor 13; .006; ppm; 13:13. Wind Speed; 9.7; mph; 13:13. Wind Direction; 173°; 13:13. |  |
| Odour Log (Thames): Wednesday 1st June 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM3 0.017ppm 00:54-01:55, OM10 0.017ppm 23:54-00:08 < 15 minutes, 0.018ppm 04:08–04:22 < 15 minutes.” Operational Issues/Causes “No odour issues on site.” Actions: No data. Thursday 2nd June 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Warm – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 0.019ppm @ 19:54 <15 mins, 0.016ppm @ 21:26 < 15 mins, 0.015ppm @ 23:56 < 15 mins.” Operational Issues/Causes: “No issues on site.” Actions: No data. Friday 3rd June 2022: AM – Warm – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “OM3 spiking all shift max 0.025ppm.” Operational Issues/Causes: ”Doors open on PST 13 & 14.” Actions: “Doors closed.” Saturday 4th June 2022: AM – Warm – Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool - Rain. All OMU’s in use. Observations/Complaints: “OM3 spiking 0.022ppm @ 23:26-23:39, 00:41-00:55 max 0.017ppm.” Operational Issues/Causes: ”No odours found.” Actions: No data. Sunday 5th June 2022: AM – Warm – Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “OM8 spiking at 16:35-16:46 but < 15 mins max 0.018ppm.” Operational Issues/Causes: “Pumping Station 17 spill being cleaned-up.” Actions: No data. PM – Rain. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Monday 6th June 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM8 0.016 7:02-7:19.” Operational Issues/Causes: ”P17 spill overnight.” Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. Tuesday 7th June 2022: AM – Warm – Sunny with patch Clouds. All OMU’s in use. Observations/Complaints: ”No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Warm – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes No data. Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 01/06/22; 0; 1068 TW figure 1129; 1030; 2098 TW figure 2159; 2057; 4155 TW figure 4215. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Being brought back into service. Digester 6 - In use – seal level approx. 4ft below coping stones – seal full of debris and other extraneous matter that has by-passed screening. Digester 7 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 8. - In use – seal level approx. 4ft below coping stones - seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 9 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling. Digester 10 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling. Digester 11 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Dry spill requires clean-up. Digester 12 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Digester 14. - In use – seal level approx. 2ft below coping stones – good seal. Tank gassing-off – noticeable odour in vicinity. Digester 15 – Out of use. Digester 16 - In use – seal level approx. 1ft below coping stones – seal weak and bubbling - seal full of debris and other extraneous matter that has by-passed screening. Dry spill requires clean-up. Digester 17 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 18 – Out of use. Digester 19 – In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 5ft below coping stones – seal weak and bubbling. |  |
| GENERAL Sludge Screening House All (pedestrian) doors closed at time of inspection. Roller shutter closed. 2x “Screws” clogged with rag require removal/cleansing. Imported Sludge Sixty (60) imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78). PST 73 drained down and undergoing maintenance. East Side Raw Sludge Screen House Doors closed at time of inspection. No.5 Pumping Station – Doors open West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Large fat deposits on surface of 9 & 10. Number 12 drained down. Large pile or rag on Service Road – noticeably odourus – requires removal. Pasteurisation Plant Ten streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste (full) & 1x 8-Yard Rag skip (covered). 1x 10-Yard Rag skip (covered) in Service Road adjacent to Power House. 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – large sludge leak around both requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. |  |

Odour Control Unit (OCU) performance monitoring – 08/06/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Yes |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.00 0.00 0.00 | 0.6 | Yes |
| Transfer PS inlet | 0.00 0.00 0.00 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.5 | Yes |
| New West inlet (OCU11) | 0.00 0.00 0.00 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 0.00 0.00 0.00 | 0.5 | Yes |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |