### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 24th May 2022 |  |
| --- | --- |
| Attendees: Mr L. Phillips (L.B. Hounslow) and Caitlin Simmonds (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and clean. Hoppers 1 and 3 were full and needed draining hopper 2 had been drained to its lowest point. Tank 1B – Tank empty clean slight grit scattered around tank needs flushing. All hoppers full and require draining. Tank 2A – Tank empty slight grit in parts of tank. All hoppers were full and need draining. Tank 2B Tank empty grit build up at top end of tank. All hoppers full and need draining. Tank 3A – Tank empty entire tank covered in grit needs flushing. All hoppers full and require draining. Tank 3B – Tank empty whole of tank covered by grit and sludge – tank needs flushing tank back-filling and all Hoppers covered by stagnant water - requires draining. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty clean slight grit in tank needs flushing. All hoppers full and need draining. Tank 6B – Tank empty clean Hoppers 1 and 3 need draining and hopper 2 is drained to its lowest point. Tank 7A – Tank empty over 50% of tank covered by grit tank requires flushing. Tank back-filling and all hoppers covered by stagnant water - requires draining. Tank 7B – Tank back-filling – 75% of Tank and all Hoppers covered by stagnant water - requires draining/over-pumping. Tank 8A – Tank empty small area of tank covered in grit tank requires flushing. Hoppers 1 and 3 were full and required draining however hopper 2 had been drained to its lowest point. Tank 8B – Tank empty clean slight grit build up. Hoppers 1 and 3 were full and needed draining Hopper 2 had been drained to its lowest point. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; 0.000; ppm; 13:13. Monitor 2; 0.001; ppm; 13:13. Monitor 3; 0.004; ppm; 13:13. Monitor 4; 0.000; ppm; 13:13. Monitor 5; 0.004; ppm; 13:13. Monitor 6; 0.000; ppm; 13:13. Monitor 7; 0.000; ppm; 13:14. Monitor 8; 0.005; ppm; 13:14. Monitor 9; 0.000; ppm; 13:14. Monitor 10; 0.000; ppm; 13:14. Monitor 11; 0.003; ppm; 13:14. Monitor 12; 0.003; ppm; 13:14. Monitor 13; 0.005; ppm; 13:14. Wind Speed; 2.416; mph; 13:14. Wind Direction; 208.036; 13:14. |  |
| *Negative response queried with TW Odour Log Tuesday 17th May 2022 DAY SHIFT Temp. Hot. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. Wednesday 18th April 2022 DAY SHIFT Temp. Warm. Weather. Cloudy W/ Sunny spells. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issue. Operational issues / causes observed. Blank. Actions Taken. Blank. Thursday 19th May 2022 DAY SHIFT Temp. Hot. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in. Time: 17:30. Observations / Customer Complaint. OM3 spiking all shift max 0.26ppm at 16:11. Operational issues / causes observed. PST area checked. Actions taken. Unable to find any odours. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM50.016 23:22 -00:22 0.020 21:52 – 22:22. Operational issues / causes observed. Odour from drain main drive. Actions taken. Blank. Friday 20th May 2022 DAY SHIFT Temp. Warm. Weather. Rain/Sunny spells. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No Odour. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM5 spiked at 11:23 – 11:37 less than 15mins duration max 0.015ppm, OM3 spiked at 22:24 -22:40 OM3 max0.014. Operational issues / causes observed. Areas checked resources of odour. Actions taken. Blank. Saturday 21st May 2022 DAY SHIFT Temp. Warm. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM5 spiked at 22:08 – 22:37 max 0.017ppm, 01:22 – 01:34- 03:05 03:22max 0.017. Operational issues / causes observed. Pasteurisation in the air and main drain checked. Actions Taken. Blank. Sunday 22nd May 2022 DAY SHIFT Temp. Warm. Weather. Sunny. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. OM5 spiked at 23:55 – 00:07 but less than 15 minutes duration max 0.015ppm. Operational issues / causes observed. Blank Actions Taken. Blank. Monday 23rd May 2022 DAY SHIFT Temp. Cool. Weather. Cloudy. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. Tuesday 24th May 2022 DAY SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. Wednesday 25th May 2022 DAY SHIFT Temp. Warm. Weather. Patchy rain. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. OM3 spiking at 19:30 – 19:40 max 0.045ppm 20:31 – 20:55max 0.017ppm Operational issues / causes observed. OCU 11 above trigger level reading 0.784max 0.045ppm. Actions Taken. Reported. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 20/05/22; 0; 2816; 1405; 4221; 1392; 5613. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 6 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 7 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 8. - was in service and had a weak sloppy seal. There was no sign of recent spillage. . Digester 9 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 10 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 11 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 12 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 13 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 14. – was in service had good thick crusty seal. There was no sign of recent spillage. Digester 15 – Out of use. Digester 16 – out of use. Digester 17 - was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 18 – Out of use. Digester 19 – was in service and had a weak sloppy seal. There was no sign of recent spillage. Digester 20 - was in service and had a weak sloppy seal. There was no sign of recent spillage. |  |
| GENERAL Sludge Screening House All (pedestrian) doors closed at time of inspection. Roller shutter partially raised as tanker discharging to screener. Imported Sludge Seventy-four (74) imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – sludge blanket covering surface of all tanks. PST 73 drained down and undergoing maintenance. East Side Raw Sludge Screen House Doors open at time of inspection. No.5 Pumping Station – Doors open West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Large fat deposits on surface of 9 & 10. Number 12 drained down – residual sludge and grit requires clean-up. Pasteurisation Plant Nine (9) streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste (full) & 1x 8-Yard Rag skip (covered). 1x 10-Yard Rag skip (covered) in Service Road adjacent to Power House. 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – sludge leak around both skips require clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. New Works (West Side) Battery E Feed Channel for Aeration Lanes – clear |  |

Odour Control Unit (OCU) performance monitoring – 25/05/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 4.40 3.57 3.98 Ave: 1.32 | 0.05 | No |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Yes |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.00 0.00 0.00 | 0.6 | Yes |
| Transfer PS inlet | 0.00 0.00 0.00 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.5 | Yes |
| New West inlet (OCU11) | 0.217 0.227 0.229 Ave:0.224 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 0.000 0.000 0.000 | 0.5 | Yes |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |