### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 17th May 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Mr Neil Bristow (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – Hopper 1 approx. 90% full , Hopper 2 in process of being over-pumped with recently hired high-volume pump, Hopper 3 approx. 60% full – requires draining/over-pumping. Tank 1B – Tank empty – Approx. 30% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 approx. 40% full, Hoppers 2 approx. 10% full - requires draining/over-pumping. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 75% full, Hoppers 2 & 3 approx. 40% full - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hopper 1 full with thick sludge crust - Hoppers 2 & 3 approx. 60% full - requires draining/over-pumping. Tank 3A – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 60% full – requires draining/over-pumping. Tank 3B – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – Tank back-filling and all Hoppers covered by stagnant water - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered and odour controlled were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 60% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – Hoppers 1 & 3 approx. 60% full, Hopper 2 approx. 25% full - requires draining/over-pumping. Tank 7A – Tank empty – Approx. 85% of tank covered by grit and sludge – requires further flushing. Tank back-filling and all Hoppers covered by stagnant water - requires draining/over-pumping. Tank 7B – Tank back-filling – 75% of Tank and all Hoppers covered by stagnant water - requires draining/over-pumping. Tank 8A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 40% full with thick sludge/grit, Hoppers 2 & 3 approx. 30% full - requires draining/over-pumping. Tank 8B – Tank empty – Approx. 40% of tank covered by grit and sludge – requires further flushing – All Hoppers full - requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:13. Monitor 2; .001; ppm; 13:13. Monitor 3; .003; ppm; 13:13. Monitor 4; .000; ppm; 13:13. Monitor 5; .005; ppm; 13:13. Monitor 6; .000; ppm; 13:13. Monitor 7; .000; ppm; 13:13. Monitor 8; .000; ppm; 13:13. Monitor 9; .000; ppm; 13:13. Monitor 10; .004; ppm; 13:13. Monitor 11; -0.025*; ppm; 13:13. Monitor 12; .006; ppm; 13:13. Monitor 13; .005; ppm; 13:13. Wind Speed; 9.1; mph; 13:13. Wind Direction; 181°; 13:13. |  |
| *Negative response queried with TW Odour Log (Thames): Wednesday 11th May 2022: AM – Cool - Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Patchy Rain. All OMU’s in use. Observations/Complaints: “OM7 0.017 MAX spikes @02:38/03:37 <15 min.” Operational Issues/Causes “odour from Main Drive.” Actions: No data. Thursday 12th May 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM3 0.026 15:10-15:25 & 0.020 12:40-12:56.” Operational Issues/Causes: “Area checked – No source discovered.” Actions: No data PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No Odour issues.” Operational Issues/Causes: No data. Actions: No data. Friday 13th May 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM3 0.028 14:40-14:45 & 0.041 16:38-16:56.” Operational Issues/Causes: “Area checked – no source found. Some odour from PAS.” Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 0.030ppm 20:03-20:25. 0.033ppm 20:33-20:55. 0.025ppm 21:03-22:54.” Operational Issues/Causes: ”Area checked. Nothing out of the ordinary detected in West Inlet Area. OCU11 discharging high odour from stack 550ppb. Chemical dosing out of range.” Actions: No data. Saturday 14th May 2022: AM – Warm – Sunny. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “OM3 0.028ppm 00:03-00:25.” Operational Issues/Causes: ”No odour issues found.” Actions: No data. Sunday 15th May 2022: AM – Warm – Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “NO ODOUR ISSUES.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Patchy Rain. All OMU’s in use. Observations/Complaints: “OM3 0.015ppm 19:55-20:10. 0.028ppm 23:54-00:25.” Operational Issues/Causes: ”No odour issues.” Actions: No data. Monday 16th May 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “OM3 0.016 11:55-12:03. 0.037 13:24-13:33. 0.033 14:54-15:10.” Operational Issues/Causes: ”Area checked no source found.” Actions: No data. PM – Cool – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 17th May 2022: AM – Hot - Sunny. All OMU’s in use. Observations/Complaints: ”No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes No data. Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 16/05/22; 20; 2441; 1405; 3866; 2048; 5914. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Being brought back into service – seal level approx. 4ft below coping stones – good seal (stones in use). Digester 6 - In use – seal level approx. 2ft below coping stones – seal weak and bubbling. Digester 7 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 8. - In use – seal level approx. 4ft below coping stones - seal weak and bubbling. Digester 9 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 10 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 11 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Digester 12 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 14. - In use – seal level approx. 3ft below coping stones – good seal. Dry spill surrounding half of Tank in process on being hosed down. Digester 15 – Out of use. Digester 16 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 17 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 18 – Out of use. Digester 19 – In use – seal level approx. 3ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. |  |
| GENERAL Sludge Screening House All (pedestrian) doors closed at time of inspection. Roller shutter partially raised as tanker discharging to screener. Imported Sludge Sixty (60) imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – sludge blanket covering surface of all tanks. PST 73 drained down and undergoing maintenance. East Side Raw Sludge Screen House Doors open at time of inspection. No.5 Pumping Station – Doors open West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Large fat deposits on surface of 9 & 10. Number 12 drained down – residual sludge and grit requires clean-up. Pasteurisation Plant Nine streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste (full) & 1x 8-Yard Rag skip (covered). 1x 10-Yard Rag skip (covered) in Service Road adjacent to Power House. 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – sludge leak around both skips requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. Rag deposit on walkway requires removal. |  |

Odour Control Unit (OCU) performance monitoring – 17/05/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.31 0.30 0.35 | 0.05 | No |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Yes |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.22 0.21 0.18 | 0.6 | Yes |
| Transfer PS inlet | 18.77 16.86 22.08 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.5 | Yes |
| New West inlet (OCU11) | 0.00 0.00 0.01 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 0.00 0.04 0.03 | 0.5 | Yes |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |