### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 26th April 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Ms Caitlin Simmonds (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – All Hoppers approx. 90% full – requires draining/over-pumping. Tank 1B – Tank empty – Approx. 30% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 40% full, Hoppers 2 & 3 approx. 20% full - requires draining/over-pumping. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 75% full, Hoppers 2 & 3 approx. 40% full - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hopper 1 full with thick sludge crust - Hoppers 2 & 3 approx. 60% full - requires draining/over-pumping. Tank 3A – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 60% full – requires draining/over-pumping. Tank 3B – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – Tank back-filling and all Hoppers covered by stagnant water - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered and odour controlled were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 80% full - requires draining/over-pumping. Tank 6B – Tank empty – Approx. 15% of tank covered by grit and sludge – requires further flushing – Hopper 1 full with thick sludge crust, Hoppers 2 & 3 approx. 50% full – requires draining/over-pumping. Tank 7A – Tank in use – No Amajets operating – Pump at location but not in operation at this time. Tank 7B – 100% of tank covered by grit and sludge – requires further flushing – Hopper 1 empty, Hoppers 2 & 3 full - requires draining/over-pumping. Tank 8A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – Hoppers 1 and 3 full, Hopper 2 approx. 80% full - requires draining/over-pumping. Tank 8B – Tank empty – Approx. 40% of tank covered by grit and sludge – requires further flushing – All Hoppers full - requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received three complaints by email in the preceding week: 19/04/22 (19:08) an email was received from Arnold Crescent area advising: “The smell of Mogden today is terrible! It is now 19.05 and is still very very strong smelling!” – OMU data for meters adjacent to this location at this time are detailed below: OMU 10 = .004ppm OMU 11 = -0.025ppm OMU12 = .007ppm OMU 13 = .010ppm 19/04/22 (16:06) an email was received from Whitton Dene area advising: “A very strong effluent smell - arguably the strongest I've smelt it since moving here in 2012. A super strong sewage smell mixed with a chemical-type smell.” – OMU data for meters adjacent to this location at this time are detailed below: OMU 10 = .006ppm OMU 11 = -0.025ppm OMU12 = .006ppm OMU 13 = .008ppm 21/04/22 (15:50) an email was received from Hall Road area advising: “bad smell especially when the wind blows also, I notice along the river the water was very cloudy and dark” – OMU data for meters adjacent to this location at this time are detailed below: OMU 10 = .005ppm OMU 11 = -0.025ppm OMU12 = .008ppm OMU 13 = .009ppm The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:43. Monitor 2; .002; ppm; 13:43. Monitor 3; .000; ppm; 13:43. Monitor 4; .007; ppm; 13:43. Monitor 5; .007; ppm; 13:43. Monitor 6; .006; ppm; 13:43. Monitor 7; .000; ppm; 13:43. Monitor 8; .003; ppm; 13:43. Monitor 9; .006; ppm; 13:43. Monitor 10; .005; ppm; 13:43. Monitor 11; -0.025*; ppm; 13:43. Monitor 12; .004; ppm; 13:43. Monitor 13; .008; ppm; 13:43. Wind Speed; 4.7; mph; 13:43. Wind Direction; 67.9°; 13:43. |  |
| *Negative response queried with TW Odour Log (Thames): Tuesday 19th April 2022: AM - Warm - Sunny. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No spikes on Trends.” Operational Issues/Causes “PAS Stream 11 reactor draining to low level.” Actions: No data. Wednesday 20th April 2022: AM – Warm – Sunny. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Thursday 21st April 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “OM13 0.022ppm 01:03-02:04.” Operational Issues/Causes: “PAS odour detected in area. No spills or overflows from PAS streams.” Actions: No data. Friday 22nd April 2022: AM – Warm – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Saturday 23rd April 2022: AM – Warm – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Sunday 24th April 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Monday 25th April 2022: AM – Warm – Patchy Rain. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 26th April 2022: AM – No data. All OMU’s in use. Observations/Complaints: No data. Operational Issues/Causes: No data. Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes No data. Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 22/04/22; 0; 1007; 1635; 2642; 1568; 4210. 25/04/22; 0; 1987; 1448; 3435; 1729; 5164. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Out of use – contractors on site working. Digester 6 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 7 - In use – seal level approx. 7ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 8. - In use – seal level approx. 5ft below coping stones - seal weak and bubbling. Digester 9 - In use – seal level approx. 7ft below coping stones - seal weak and bubbling. Digester 10 - In use – seal level approx. 7ft below coping stones - seal weak and bubbling. Digester 11 - In use – seal level approx. 5ft below coping stones - seal weak and bubbling. Digester 12 - In use – seal level approx. 6ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling. Digester 14. - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 15 – Out of use. Digester 16 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 17 - In use – seal level approx. 5ft below coping stones – seal weak and bubbling. Digester 18 – Out of use. Digester 19 – In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 5ft below coping stones – seal weak and bubbling. |  |
| GENERAL Sludge Screening House All doors closed at time of inspection. “Screw” from previous repairs - covered in rag - outside Screening House – requires removal. Imported Sludge Forty (40) imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – sludge blanket covering surface of all tanks – in addition observed on FST’s 61-63. East Side Raw Sludge Screen House Doors closed at time of inspection. Pasteurisation Plant Eight streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste & 1x 8-Yard Rag skip (covered). New signage added to skip area to clearly identify skip contents. 1x 10-Yard Rag skip (covered) in Service Road adjacent to Power House. 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant – sludge leak around both skips requires clean-up. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use. Large fat deposits on surface of 9 & 10. Number 12 drained down – residual sludge and grit requires clean-up. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. |  |

Odour Control Unit (OCU) performance monitoring – 28/04/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | 29.88 27.32 28.11 | Unknown | Unknown |
| Main pumping station outlet | No data | 0.2 | Unknown |
| East OCU | 0.02 0.00 0.00 | 0.05 | Yes |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Yes |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.098 0.092 0.081 | 0.6 | Yes |
| Transfer PS inlet | 92.18 91.31 86.81 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.5 | Yes |
| New West inlet (OCU11) | 3.21 3.09 3.06 | 0.5 | No |
| Pasteurisation Plant (OCU12) | 0.00 0.00 0.00 | 0.5 | Yes |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |

Data provided for OCU readings queried with TW as some non-compliant

and significant variation – possible error with readings taken as ppb not ppm (?)