### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 12th April 2022 |  |
| --- | --- |
| Attendees: Mr L. Phillips (L.B. Hounslow) and Ms Roxanne Denny (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A - Was empty clean. All Hoppers full and require draining. Tank 1B - Was empty clean slight grit hopper end of tank. Hoppers 1 and 2 drained to lowest point hopper 3 full and requires draining. Tank 2A - Was empty clean slight grit hopper end of tank. Hoppers 2 and 3 drained to lowest point. Hopper 1 full and requires draining. Tank 2B - Was empty clean slight grit throughout tank. All hoppers full and require draining no odour detected. Tank 3A - Was empty covered in grit and sludge tanks needs flushing. All hoppers full and require draining no odour detected. Tank 3B – Was empty tank covered in grit and sludge and requires flushing. Hopper end of tank part filled all hoppers full and require draining. Tanks 4A, 4B, 5A & 5B which are covered, and odour controlled were all in use - unable to gauge condition as lighting system still not working. Tank 6A - Was empty clean slight grit in tank. All hoppers full and require draining no odour detected. Tank 6B - Was empty clean slight grit in tank. All hoppers full and require draining no odour detected. Tank 7A - All Amajets operating in process of being returned. Tank 7B - Was empty clean hopper end of tank part filled and requires draining. Tank 8A - Was empty clean all hoppers full and require draining no odours detected. Tank 8B - Was empty clean all hoppers full and require draining no odours detected. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; 0.000; ppm; 13:43. Monitor 2; 0.002; ppm; 13:43. Monitor 3; 0.003; ppm; 13:43. Monitor 4; 0.005; ppm; 13:43. Monitor 5; 0.007; ppm; 13:43. Monitor 6; 0.006; ppm; 13:43. Monitor 7; 0.000; ppm; 13:43. Monitor 8; 0.003; ppm; 13:43. Monitor 9; 0.004; ppm; 13:43. Monitor 10; 0.000; ppm; 13:43. Monitor 11; -0.025*; ppm; 13:43. Monitor 12; 0.005; ppm; 13:43. Monitor 13; 0.007; ppm; 13:43. Wind Speed; 2.642; mph; 13:43. Wind Direction; 228.776°; 13:43. |  |
| *Negative response queried with TW Odour Log (Thames): Odour Log Wednesday 06th April 2022 DAY SHIFT Temp. Warm. Weather. Cloudy. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30 Observations / Customer Complaint. No odour issues. Operational issues / causes observed Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Rain. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. Thursday 07th April 2022 DAY SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. apart from OM11. Odour Readings. All OMU’s in operation Time: 05:30. Observations / Customer Complaint. OM5 spiked at 00:35 – 00:50 max 0.22ppm and at 02:06 – 02:19 but 15mins duration max. Operational issues / causes observed. Slight odour from Pasteurisation in the air. Actions Taken. Blank. Friday 08th April 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Patchy rain. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. Saturday 09th April 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No Odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. Sunday 10th April 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patch clouds. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. Monday 11th April 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. No odours issues found or reported. Operational issues / causes observed. Blank Actions Taken. Blank. Tuesday 12th April 2022 DAY SHIFT Temp. Warm. Weather. Overcast night. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. Wednesday 13th April 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ Patchy clouds. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast night. Odour Readings. All OMU’s in operation apart from OM11. Time: 05:30. Observations / Customer Complaint. OM5 spiked at 03:36 – 03:51max 0.018ppm. Operational issues / causes observed. Blank. Actions Taken. Blank Thursday 14th April 2022 DAY SHIFT Temp. Warm. Weather. Sunny W/ patchy clouds. Odour Readings. All OMU’s in operation apart from OM11. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions taken. Blank. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 08/04/2022; 39; 656; 1823; 2518; 1744; 4262. 12/04/2022; 98; 1549; 2011; 3658; 1088; 4746. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Out of use. Digester 6 - In use weak seal no signs of previous spillage. Digester 7 - In use weak seal no signs of previous spillage. Digester 8 - In use weak seal no signs of previous spillage. Digester 9 - In use weak seal no signs of previous spillage. Digester 10 - In use weak seal no signs of previous spillage. Digester 11 - In use weak seal no signs of previous spillage. Digester 12 - In use weak seal no signs of previous spillage. Digester 13 - In use weak seal no signs of previous spillage. Digester 14 - In use weak seal no signs of previous spillage. Digester 15 - Out of use. Digester 16 - In use – weak foamy seal ongoing spill requiring anti-foam and clean up. Digester 17 - In use weak seal no signs of previous spillage. Digester 18 – Out of use. Digester 19 – In use weak seal no signs of previous spillage. Digester 20 - In use weak seal no signs of previous spillage. |  |
| GENERAL Sludge Screening House All doors closed at time of inspection. Imported Sludge 0 imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – sludge blanket covering surface of all tanks – in addition observed on FST’s 61-63. East Side Raw Sludge Screen House Doors closed at time of inspection. Pasteurisation Plant Eight streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste,1x 8-Yard Rag skip (covered) & 1x Rag container skip (covered). New signage added to skip area to clearly identify skip contents. 1x 10-Yard Rag skip (covered) in Service Road adjacent to Powerhouse. 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use, Number 12 drained down. Large fat deposits on surface of 9 & 10. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. |  |

Odour Control Unit (OCU) performance monitoring – 12/04/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.152 0.131 0.000 0.010 | 0.2 | No |
| East OCU | 0.263 0.211 0.186 0.007 | 0.05 | No |
| West inlet OCU | 0.265 0.217 0.186 0.222 | 0.05 | No |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.148 0.000 0.000 0.04 | 0.6 | No |
| Transfer PS inlet | 0.000 0.000 0.000 0.000 | Unknown | Unknown |
| Transfer PS outlet | 0.147 0.144 0.143 0.144 | 0.5 | No |
| New West inlet (OCU11) | 0.243 0.206 0.186 0.211 | 0.5 | No |
| Pasteurisation Plant (OCU12) | 0.125 0.000 0.000 0.041 | 0.5 | No |
| GBT Plant OCU Outlet | 0.275 0.220 0.189 0.228 | Unknown | Unknown |