### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 5th April 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and Ms Caitlin Simmonds (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – All Hoppers approx. 90% full – requires draining/over-pumping. Tank 1B – Tank empty – Approx. 30% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 20% full - requires draining/over-pumping - Hoppers 2 & 3 empty. Tank 2A – Tank empty – Approx. 20% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 20% full - requires draining/over-pumping. Tank 2B – Tank empty – Approx. 50% of tank covered by grit and sludge – requires further flushing – Hopper 1 full - Hoppers 2 & 3 approx. 60% full - requires draining/over-pumping. Tank 3A – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 80% full – requires draining/over-pumping. Tank 3B – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – Hopper 1 full - Hoppers 2 & 3 approx. 60% full - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered and odour controlled were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers full – requires draining/over-pumping. Tank 6B – Tank empty – Approx. 15% of tank covered by grit and sludge – requires further flushing – Hopper 1 full, Hoppers 2 & 3 approx. 75% full – requires draining/over-pumping. Tank 7A – Tank in use – All Amajets operating – in process of being returned. Tank 7B – Tank backfilling – approx. 50% covered - requires draining/over-pumping. Tank 8A – Tank backfilling – approx. 50% covered - requires draining/over-pumping. Tank 8B – Tank backfilling – approx. 40% covered - requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .000; ppm; 13:43. Monitor 2; .002; ppm; 13:43. Monitor 3; .007; ppm; 13:43. Monitor 4; .005; ppm; 13:43. Monitor 5; .005; ppm; 13:43. Monitor 6; .005; ppm; 13:43. Monitor 7; .000; ppm; 13:43. Monitor 8; .003; ppm; 13:43. Monitor 9; .004; ppm; 13:43. Monitor 10; .004; ppm; 13:43. Monitor 11; -0.025*; ppm; 13:43. Monitor 12; .006; ppm; 13:43. Monitor 13; .008; ppm; 13:43. Wind Speed; 16.8; mph; 13:43. Wind Direction; 248°; 13:43. |  |
| *Negative response queried with TW Odour Log (Thames): Wednesday 30th March 2022: AM – Warm – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Thursday 31st March 2022: AM – Cold – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Cold – Cloudy. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Friday 1st April 2022: AM – Cold – Cloudy with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cold – Clear Night. All OMU’s in use. Observations/Complaints: “OM4 0.016ppm 20:07-21:04.” Operational Issues/Causes: “Power House area checked. No odour detected.” Actions: No data. Saturday 2nd April 2022: AM – Cold – Sunny with Patch Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Freezing– Clear Night. All OMU’s in use. Observations/Complaints: “OM10 0.021ppm 23:04-23:13 & 0.026ppm 00:49-01:04. OM3 0.021ppm 22:40-23:27 & 0.016ppm 03:57 <15 minutes. OM5 0.015ppm 03:20 <15 minutes.” Operational Issues/Causes: “Digester Area checked. No sludge spills. Digester Bell heights high on occasion but waste gas burner controlling gas levels.” Actions: No data. Sunday 3rd April 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cold – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Monday 4th April 2022: AM – Cool – Rain. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 15th March 2022: AM – Cool – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cold – Overcast Night. All OMU’s in use. Observations/Complaints: “OM3 0.018ppm 19:54-20:09 & 0.024ppm 00:51-01:07.” Operational Issues/Causes “West Inlet Area checked. No odour detected.” Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 01/04/22; 78; 1115; 2011; 3204; 456; 3660. 04/04/22; 39; 1405; 1780; 3224; 3268; 6492. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Out of use – contractors on site working. Digester 6 - In use – seal level approx. 2ft below coping stones – seal weak and bubbling. Digester 7 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 8. - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 9 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Digester 10 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling. Digester 11 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Digester 12 - In use – seal level approx. 5ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 14. - In use – seal level approx. 3ft below coping stones - seal weak and bubbling. Digester 15 – Out of use. Digester 16 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up. Digester 17 - In use – seal level approx. 5ft below coping stones – seal weak and bubbling. Digester 18 – Out of use. Digester 19 – In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 3ft below coping stones – seal weak and bubbling. |  |
| GENERAL Sludge Screening House All doors closed at time of inspection. Imported Sludge Seventeen (17) imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – sludge blanket covering surface of all tanks – in addition observed on FST’s 61-63. East Side Raw Sludge Screen House Doors closed at time of inspection. Pasteurisation Plant Eight streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste,1x 8-Yard Rag skip (covered) & 1x Rag container skip (covered). New signage added to skip area to clearly identify skip contents. 1x 10-Yard Rag skip (covered) in Service Road adjacent to Power House. 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use, Number 12 drained down. Large fat deposits on surface of 9 & 10. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. |  |

Odour Control Unit (OCU) performance monitoring – 05/04/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.319 0.223 0.158 | 0.2 | No |
| East OCU | 0.309 0.198 0.133 | 0.05 | No |
| West inlet OCU | 0.340 0.218 0.154 | 0.05 | No |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.299 0.193 0.137 | 0.6 | No |
| Transfer PS inlet | 0.726 0.231 0.156 | Unknown | Unknown |
| Transfer PS outlet | 0.308 0.185 0.130 | 0.5 | No |
| New West inlet (OCU11) | 0.304 0.213 0.157 | 0.5 | No |
| Pasteurisation Plant (OCU12) | 0.594 0.593 0.474 | 0.5 | No |
| GBT Plant OCU Outlet | 0.319 0.204 0.204 | Unknown | Unknown |

Data provided for OCU readings queried with TW as all non-compliant

as displayed – possible error with readings taken as ppb not ppm (?)