### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 15th March 2022 |  |
| --- | --- |
| Attendees: Mr Steven Maunders (L.B. Hounslow) and 2x Unknown Day Operatives (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty and flushed clean – Hopper 1 approx. 30% full – requires draining/over-pumping, Hoppers 2 & 3 empty. Tank 1B – Tank empty – Approx. 25% of tank covered by grit and sludge – requires further flushing – Hopper 1 approx. 80% full, Hoppers 2 & 3 full – requires draining/over-pumping. Tank 2A – Tank in use – No Amajets operating – requires draining down/over-pumping. Tank 2B – Tank in use – No Amajets operating – requires draining down/over-pumping. Tank 3A – Tank empty – 100% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 80% full – requires draining/over-pumping. Tank 3B – Tank in use – No Amajets operating – requires draining down/over-pumping. Tanks 4A, 4B, 5A & 5B which are covered and odour controlled were all in use - unable to gauge condition as lighting system still not working. Tank 6A – Tank empty and flushed clean – All Hoppers approx. 90% full – requires draining/over-pumping. Tank 6B – Tank empty – Approx. 10% of tank covered by grit and sludge – requires further flushing – Hopper 1 full, Hoppers 2 & 3 approx. 75% full – requires draining/over-pumping. Tank 7A – Tank in use – All Amajets operating – in process of being returned. Tank 7B – Tank empty – 80% of tank covered by grit and sludge – requires further flushing – All Hoppers full – requires draining/over-pumping. Tank 8A – Tank empty - Approx. 10% of tank covered by grit and sludge – requires further flushing – All Hoppers approx. 90% full – requires draining/over-pumping. Tank 8B – Tank empty - Approx. 25% of tank covered by grit and sludge – requires further flushing – All Hoppers full – requires draining/over-pumping. Feed Channel - The level of effluent in both feed channels was approximately 20% capacity - no local odours. |  |
| Complaints The Council directly received no complaints by telephone in the preceding week. The Council directly received no complaints by email in the preceding week: The Council received no complaints by email from MRAG. Thames Water controller advised that they had received no direct complaints in the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; .003; ppm; 13:19. Monitor 2; .002; ppm; 13:19. Monitor 3; .005; ppm; 13:19. Monitor 4; .006; ppm; 13:19. Monitor 5; .006; ppm; 13:19. Monitor 6; .007; ppm; 13:19. Monitor 7; .000; ppm; 13:19. Monitor 8; .004; ppm; 13:19. Monitor 9; .005; ppm; 13:19. Monitor 10; .000; ppm; 13:19. Monitor 11; .000; ppm; 13:19. Monitor 12; .000; ppm; 13:19. Monitor 13; .000; ppm; 13:19. Wind Speed; 4.4; mph; 13:19. Wind Direction; 93.2°; 13:19. |  |
| Odour Log (Thames): Wednesday 9th March 2022: AM – Warm – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “OM11 0.019ppm 21:37-22:37.” Operational Issues/Causes: “Area checked. Sludge spill around PAS stream 12.” Actions: “Day Ops called out to wash area down.” Thursday 10th March 2022: AM – Cool – Sunny with Patchy Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data PM – Cold – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Friday 11th March 2022: AM – Cool – Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “OM11 spiked at 09:53-10:51 max 0.018ppm.” Operational Issues/Causes: “Digester No.16 gassing off. VHP No.3 shut down for oil change. Flare-stack running.” Actions: No data. PM – Cool – Rain. All OMU’s in use. Observations/Complaints: “OM11 0.022 23:07-23:23.” Operational Issues/Causes: “Dig. 16 gassing off”. Actions: No data. Saturday 12th March 2022: AM – Warm – Sunny with Patch Clouds. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool– Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Sunday 13th March 2022: AM – Warm – Rain with Sunny Spells. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Monday 14th March 2022: AM – Cool – Sunny with Patch Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cold – Clear Night. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. Tuesday 15th March 2022: AM – Cool – Sunny with Patch Clouds. All OMU’s in use. Observations/Complaints: “No odour issues.” Operational Issues/Causes: No data. Actions: No data. PM – Cool – Overcast Night. All OMU’s in use. Observations/Complaints: “No odour issues found or reported.” Operational Issues/Causes No data. Actions: No data. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 09/03/22; 59; 1321; 2532; 3912; 1896; 5808. 15/03/22; 117; 4275; 3784; 8176; 6551; 14727. The sludge stock levels for the West side circular primary settlement tank 1 were compliant with the OMP trigger level (500m3) for all of the dates for which data has been provided. There are no limits for the East side primary settlement tanks as these are covered and odour controlled. Thames is required by the terms of the abatement notice agreed in 2005 to notify LBH on the next working day of any such exceedance and notify LBH within three working days of any appropriate remedial measure taken. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – Out of use – contractors on site working. Digester 6 - In use – seal level approx. 2ft below coping stones – seal weak and bubbling – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 7 - In use – seal level approx. 6ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 8. - In use – seal level approx. 7ft below coping stones - seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 9 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 10 - In use – seal level approx. 5ft below coping stones - seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 11 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling. Digester 12 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling. Digester 13 - In use – seal level approx. 4ft below coping stones - seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 14. - In use – seal level approx. 4ft below coping stones - seal weak and bubbling – Bell height high requiring draw down of Biogas. Digester 15 – Out of use. Digester 16 - In use – seal level approx. 4ft below coping stones – seal weak and bubbling vigorously – ongoing spill requiring anti-foam and clean-up – Bell height high requiring draw down of Biogas. Digester 17 - In use – seal level approx. 6ft below coping stones – seal weak and bubbling. Digester 18 – Out of use. Digester 19 – In use – seal level approx. 5ft below coping stones – seal weak and bubbling. Digester 20 - In use – seal level approx. 5ft below coping stones – seal weak and bubbling. |  |
| GENERAL Sludge Screening House One door open – contractor working on screen. Imported Sludge Zero imports across preceding seven days. # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78). East Side Raw Sludge Screen House Doors closed at time of inspection. Pasteurisation Plant Eight streams running. Skips 2x small (blue) skips – rear of sludge screen house both empty. 1x open container grit skip (empty) uncovered, 1x open container skip – General Waste (empty),1x 10-Yard Rag skip (covered). New signage added to skip area to clearly identify skip contents. 1x 10-Yard Rag skip (covered) in Service Road adjacent to Power House. 1x open container grit skip (empty) uncovered & 1x open 8-Yard skip (scrap metal) in Service Road by Pasteurisation Plant. 2x 8-Yard skips – Rag (covered) by Sludge Handling Area by Pasteurisation Plant. 1x 10-Yard enclosed General Waste skip in Service Road at rear of East Raw Sludge Screening House. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues Circular PST’s 9, 10 & 11 in use, Number 12 drained down. Large fat deposits on surface of 9 & 10. New Works (West Side) Battery E Feed Channel for Aeration Lanes – Channel blocked from Aeration Lane 22 – requires jetting. Tank performance progressively improving. |  |

Odour Control Unit (OCU) performance monitoring – 15/03/22

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | No data | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| West inlet OCU | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | No data | Unknown | Unknown |
| Sludge reception outlet | No data | 0.8 | Unknown |
| Thickening plant inlet | No data | Unknown | Unknown |
| Thickening plant outlet | 0.11 0.05 0.09 | 0.6 | No |
| Transfer PS inlet | 18.09 17.89 16.77 | Unknown | Unknown |
| Transfer PS outlet | 0.00 0.00 0.00 | 0.5 | Yes |
| New West inlet (OCU11) | 0.00 0.00 0.00 | 0.5 | Yes |
| Pasteurisation Plant (OCU12) | 0.003 0.001 0.002 | 0.5 | Yes |
| GBT Plant OCU Outlet | 0.00 0.00 0.00 | Unknown | Unknown |