### Mogden Sewage Treatment Works

### TW Site Inspection

| Date of inspection: 21 March 2023 |  |
| --- | --- |
| Attendees: Kumail Haider (L.B. Hounslow) and Miss Emma McDonald (Thames Water) |  |
| LB Hounslow Observation | Thames Water Action / Response |
| Storm Water Storage Tanks (SWST) Tank 1A – Tank empty clean. However, all Hoopers are 80% full and require draining. Tank 1B – Tank empty around 30% of tank covered in grit and sludge. tank requires flushing, Hopper 1&2 approx 40% full- requires draining/over-pumping. Tank 2A – Tank requires flushing 20% covered in grit, all Hoppers 60% full requires draining/over-pumping. Tank 2B – Tank requires flushing 30% covered in grit/sludge, all Hoppers 80% full requires draining/over-pumping. Tank 3A – Tank 60% covered by grit and sludge – requires further flushing – All Hoppers approx 70% full - requires draining/over-pumping Tank 3B – Tank 40% covered by grit and sludge – requires further flushing – All Hoppers full - requires draining/over-pumping. Tanks 4A, 4B, 5A & 5B are covered, and odour controlled, were all in use - unable to measure condition as lighting system still not working. Tank 6A – Tank 20% covered by grit and sludge – requires further flushing – all Hoppers approx. 50% full - requires draining/over-pumping. Tank 6B – Tank 30% covered by grit and sludge – Hoppers 1&2 (30%) & 3 (80%) requires further flushing. Tank 7A – Tank 40% full in process of being returned to works –all Amajets in operation. Tank 7B – Tank 50% covered by effluent, grit and sludge – requires further flushing. Tank 8A – Tank 40% covered by grit and sludge – requires further flushing/over pumping. Tank 8B – Tank empty around 50% of tank covered in grit and sludge. tank needs further flushing. All hoppers full and require draining/over pumping. Feed Channel - The level of effluent in both feed channels was approximately 15% capacity. # Sludge Dip Records Date; West PSTs 1; West PSTs 2; West PSTs 3; West Total; East PSTs; Grand Total. All units in m3. OMP limit; 500. 16/03/2023; 0; 1903; 412; 2315; 3074; 5389. 17/03/2023; 0; 1757; 412; 2169; 3411; 5580. 20/03/2023; 20; 1612; 267; 1899; 3074; 4973. 21/03/2023; 88; 2212; 412; 2712; 1216; 3928. | Thames' response: - Day ops/tankers to overpump storm tanks and hoppers when possible. Due to winter weather and heavy rain the storm tanks are frequently in use at the moment, but we are coming up with a plan to overpump and flush these when weather permits - Longer-term, project being scoped to address the storm tank non-return valve replacement and upgrade the borger pump, estimated cost £160,000 and beginning May 2023 |
| Complaints The Council received no complaints by email from MRAG in the preceding week. Thames Water controller advised that they had received no direct complaints in the preceding week. The Council directly received no complaints by email in the preceding week. The Council received 0 online complaints and 0 out of hour calls during the preceding week. Odour Monitors The odour readouts (H2S) for all monitors which were providing data at time of inspection: Monitor 1; 0.004; ppm; 13.10. Monitor 2; 0.001; ppm. Monitor 3; 0.004; ppm. Monitor 4; 0.004; ppm. Monitor 5; 0.004; ppm. Monitor 6; 0.007; ppm. Monitor 7; 0.000; ppm. Monitor 8; 0.007; ppm. Monitor 9; 0.005; ppm. Monitor 10; 0.006; ppm. Monitor 11; 0.005; ppm. Monitor 12; 0.005; ppm. Monitor 13; 0.000; ppm. Wind Speed; 12.54; MPH. Wind Direction; 189.12; DEG. |  |
| Odour Log (Thames): Wednesday 15 March 2023 DAY SHIFT Temp. Cool. Weather. Cloudy. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues found or reported. Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather Clear Night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank. Actions Taken. Blank. Thursday 16 March 2023 DAY SHIFT Temp. Cool. Weather. Rain w/Sunny Spells. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues Operational issues / causes observed. Blank. Actions Taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Clear night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. Blank Actions Taken. Blank. Friday 17 March 2023 DAY SHIFT Temp. Warm. Weather. Rain w/Sunny Spells Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues Operational issues / causes observed. Blank Actions taken. Blank NIGHT SHIFT Temp. Cool. Weather. Overcast Night. Odour Readings. All OMU’s in operation. Time: 06:30. Observations / Customer Complaint. No odour issues found or reported Operational issues / causes observed. Blank Actions taken. Blank. Saturday 18 March 2023 DAY SHIFT Temp. Warm. Weather. Rain w/Sunny Spells Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Patchy Rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported Operational issues / causes observed. Blank. Actions taken. Blank. Sunday 19 March 2023 DAY SHIFT Temp. Cool. Weather. Cloudy w/Sunny Spells. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. OM8 & 9 spiked to 0.015ppm both spikes<15 minute duration Operational issues / causes observed. Blank. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Overcast Night. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No odour issues found or reported Operational issues / causes observed. Blank. Actions Taken. Blank. Monday 20 March 2023 DAY SHIFT Temp. Warm. Weather. Cloudy w/Sunny Spells. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. No odour issues found or reported. Actions taken. Blank. NIGHT SHIFT Temp. Cool. Weather. Patchy Rain. Odour Readings. All OMU’s in operation. Time: 05:30. Observations / Customer Complaint. No issues found or reported Operational issues / causes observed. Blank. Actions Taken. Blank. Tuesday 21 March 2023 DAY SHIFT Temp. Cool. Weather. Cloudy w/Sunny Spells. Odour Readings. All OMU’s in operation. Time: 17:30. Observations / Customer Complaint. No odour issues. Operational issues / causes observed. No odour issues found or reported. Actions taken. Blank. |  |
| Digesters Digesters 1-4 – Out of use (permanent). Digester 5 – In use – seal level approx. 1ft below coping stones - seal weak and bubbling. Digester 6 – In use – seal level approx. 1.5 ft below coping stones - seal weak and bubbling. Bell high gas drawn down required. Digester 7 - In use – seal level approx. 2ft below coping stones - seal weak bubbling and spilling over coping stone. Digester 8 - In use – seal level approx. 1.5ft below coping stones - seal weak and bubbling, bell high gas draw down required Digester 9 - In use – seal level approx. 1ft below coping stones - seal weak and bubbling. Digester 10 - In use – seal level approx. 2ft below coping stones - Seal weak, spilling over coping stone and bell high gas draw down required Digester 11 - In use – seal level approx. 1.5ft below coping stones - Seal weak and bubbling. Digester 12 - In use – seal level approx. 2ft below coping stones - Seal weak and bubbling Digester 13 - In use – seal level approx. 1.5ft below coping stones – seal weak and bubbling Digester 14 – Out of use. Digester 15 – Out of use. Digester 16 – Out of use. Digester 17 - In use – seal level approx. 2ft below coping stones - seal weak and bubbling. Digester 18 – In use – seal level approx. 1.5ft below coping stones - Seal weak bubbling. Digester 19 – In use – seal level approx. 3ft below coping stones - seal good. Digester 20 - In use – seal level approx. 2ft below coping stones - seal good. | Thames' response: - PCEs to draw down digesters 7, 8 and 10 - Day ops to clean spills round digesters 7 and 10 |

| GENERAL Sludge Screening House 1x (pedestrian) door open at time of inspection. Roller shutter currently missing and awaiting replacement following damage – opening has been screened temporarily. Imported Sludge No data # Final Settlement Tanks East Side of Works The 8 circular tanks previously used as PSTs are now being used as final tanks (71-78) – no issues. East Side Raw Sludge Screen House Doors open at time of inspection no contractors working. West Side Aeration Lanes (Old) Battery C aeration feed channel 100% obstructed in one channel (left) – requires jetting (TW advise that there is continuing flow below surface). West side primary settlement tanks (PST) Rectangular PSTs – no issues. Circular PST’s 9-11 in use and 12 drained down. New Works (West Side) Battery E E-battery aeration lane no blockage. Pasteurisation Plant Streams 2, 7, 8, 10 and 11 out of service. Skips 1x 8-Yard skips – Rag (covered) by Sludge Area Thames advised to check for possible contamination and removal. 1x 10-Yard contaminated General Waste skip in Service Road at rear of Raw Sludge Screening Area. | Thames' response: - Tarpaulin ordered - Doors to pumping station and raw sludge screening area to be shut - Raw sludge screening skip to be collected and reminders about its use sent |
| --- | --- |

Odour Control Unit (OCU) performance monitoring: 21/03/2023

| Plant | Reading (ppm) | Action Level (ppm) | Compliant |
| --- | --- | --- | --- |
| Main pumping station inlet | Not done by TW due to resource issues | Unknown | Unknown |
| Main pumping station outlet | 0.00 0.00 0.00 | 0.2 | Yes |
| East OCU | 0.063 0.061 0.061 | 0.05 | No |
| West inlet | 0.00 0.00 0.00 | 0.05 | Yes |
| Sludge reception inlet | - | - | - |
| Sludge reception outlet | - | - | - |
| Thickening plant inlet | - | - | - |
| Thickening plant outlet | 0.004 0.004 0.003 | 0.6 | Yes |
| New West inlet (OCU 11) | 0.016 0.017 0.016 | 0.5 | Yes |
| Pasteurization (OCU 12) | 2.358 2.301 2.325 | 0.5 | No |
| Transfer PS inlet | 0.514 0.988 0.741 | - | - |
| Transfer PS outlet | 0.006 0.020 0.020 | 0.6 | Yes |
| GBT Plant OCU Outlet | 0.006 0.008 0.007 | - | - |